## Cover Sheet
Equipment Module (EM) Specification
EM_PUR_TCU
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. Morimatsu |  | Revision
M2 Project |  |  | PP20-0098-T-004223 |  | 0.1a
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2020-12-10 |  | 王树深
Morimatsu approved: | 张予婧 | 2020-12-10 |  | 张予婧
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Equipment Module (EM) Specification provides the description for all Equipment Module Classes to be implemented in the DeltaV DCS Software. All required Equipment Module Classes are specified in this document.
2. | Method
The Equipment Module (EM) Specification is subdivided into two sections for the a Physical Part and for the Procedural Part.
The section for the Physical Part identifies the Unit Classes which will use the Equipment Module Class, and all Devices that are part of the Equipment Module. The Spread Sheet identifies by X all Devices that belong to the Equipment Module. Devices are all used actuators and PID control loops.
For valves the following informations are added to the Tag name, if applicable: NO
| NO | Valves with "normaly open" state
| FB | Valves with physical feedback signal
The section for the Procedural Part specifies all required Equipment Module Commands in a matrix which shows the activation of the individual devices per EM Command. The following keys are used for identification of the control state of the devices:
| 0 | Valve closed (also for NO valves), Motor/Pump stopped
| 1 | Valve open (also for NO valves), Motor/Pump running
| 0d | Valve closes with delay, Motor/Pump stops with delay
| 1d | Valve opens with delay, Motor/Pump starts with delay
| c | Valve/Motor/Pump controlled by PID control loop
| p | Valve pulsed
| RCAS | PID control loop operates in closed loop mode with setpoint from phase
| ROUT | PID control loop operates in open loop mode with direct control of output from phase
3. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| EM | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | EM_TOP_VALVES_1
| EM-Command | max. 16 characters, capital letters, _ for delimiter |  |  | SIP_XFER_OUT
4. | Change Log
The Equipment Module Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done only if Equipment Module Classes are added or deleted, and for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-31 | 王树深
| 0.1a | 2020-12-10 | 王树深 | 增加EM_PUR_PS

## Table
NO | Original Name | Changed Name
1 | EM_TCU
2 | EM_PUR_PS

## EM_SPRAY_BALLS_2 (hidden)
EM_SPRAY_BALLS_2
Unit Class |  | AV904 FB | AV905 FB
Buffer Hold Tanks |  | X | X
Equipment Module Command |  |  |  | Description
1 | CLOSE | 0 | 0 | All valves closed
2 | SPRAY_BALL_1 | 1 | 0 | Open Flow path to spray ball 1
3 | SPRAY_BALL_2 | 0 | 1 | Open Flow path to spray ball 2
4 | SPRAY_BALL_1_2 | 1 | 1 | Open Flow path to spray ball 1 and 2 in parallel
5 | SIP_SPRAYBALLS | a) | a) | Toggling of spray balls during CIP
6
7
8
9
10
Notes:
a)
b)
c)

## EM_POU_P1R_1 (hidden)
Table!A1
EM_POU_P1R_1
Unit Class |  | AV138 | AV665 | AV666
Puffusion 1 Room_1 |  | X | X | X
Equipment Module Command |  |  |  |  | Description
0 | HOLD | 0 | 0 | 0
1 | CLOSE | 0 | 0 | 0
2 | CIP_LINE | 1 | 1 | 0 | cip line from main pipe to pou
3 | SIP_LINE | 1 | 0 | 1 | sip line from main pipe to pou
4 | CHROMA | 1 | 0 | 0 | liquid line from main pipe to pou
5
6
7
8
9
10
11
Notes:
a)
b)
c)

## EM_POU_P1R_3 (hidden)
Table!A1
EM_POU_P1R_3
Unit Class |  | AV121 | AV166 | AV167 | AV669 | AV670
Puffusion 1 Room_3 |  | X | X | X | X | X
Equipment Module Command | [6 empty] | Description
0 | HOLD | 0 | 0 | 0 | 0 | 0
1 | CLOSE | 0 | 0 | 0 | 0 | 0
2 | CIP_LINE | 1 | 0 | 0 | 1 | 0 | cip line from main pipe to pou
3 | SIP_LINE | 1 | 0 | 0 | 0 | 1 | sip line from main pipe to pou
4 | SIP_PRESSURIZE | 1 | 0 | 0 | 0 | 0 | liquid line from main pipe to pou not open pou valve
5 | CIP_CHROMA | 0 | 0 | 1 | 0 | 0 | cip chroma commad from chroma
6 | CHROMA | 1 | 1 | 0 | 0 | 0 | open pou valve
7
8
9
10
11
Notes:
a)
b)
c)

## EM_POU_P1R4_P2R2 (hidden)
Table!A1
EM_POU_P1R4_P2R2
Unit Class
EM_POU_P1R_4 |  | AV134 | AV168 | AV169 | AV671 | AV672
EM_POU_P2R_2 |  | AV132 | AV161 | AV162 | AV663 | AV664
|  | X | X | X | X | X
Equipment Module Command | [6 empty] | Description
0 | HOLD | 0 | 0 | 0 | 0 | 0
1 | CLOSE | 0 | 0 | 0 | 0 | 0
2 | CIP_LINE | 1 | 0 | 0 | 1 | 0 | cip line from main pipe to pou
3 | SIP_LINE | 1 | 0 | 0 | 0 | 1 | sip line from main pipe to pou
4 | SIP_PRESSURIZE | 1 | 0 | 0 | 0 | 0 | liquid line from main pipe to pou not open pou valve
5 | CIP_CHROMA | 0 | 0 | 1 | 0 | 0 | cip chroma commad from chroma
6 | CHROMA | 0 | 1 | 0 | 0 | 0 | open pou valve
7
8
9
10
11
Notes:
a)
b)
c)

## EM_POU_P2R_1 (hidden)
Table!A1
EM_POU_P2R_1
Unit Class |  | AV137 | AV657 | AV658
Puffusion 2 Room_1 |  | X | X | X
Equipment Module Command |  |  |  |  | Description
0 | HOLD | 0 | 0 | 0
1 | CLOSE | 0 | 0 | 0
2 | CIP_LINE | 1 | 1 | 0 | cip line from main pipe to pou
3 | SIP_LINE | 1 | 0 | 1 | sip line from main pipe to pou
4 | CHROMA | 1 | 0 | 0 | liquid line from main pipe to pou
5
6
7
8
9
10
11
Notes:
a)
b)
c)

## EM_POU_P2R_2 (hidden)
Table!A1
EM_POU_P2R_2
Unit Class |  | AV132 | AV161 | AV162 | AV663 | AV664
Puffusion 2 Room_2 |  | X | X | X | X | X
Equipment Module Command | [6 empty] | Description
0 | HOLD | 0 | 0 | 0 | 0 | 0
1 | CLOSE | 0 | 0 | 0 | 0 | 0
2 | CIP_LINE | 1 | 0 | 0 | 1 | 0 | cip line from main pipe to pou
3 | SIP_LINE | 1 | 0 | 0 | 0 | 1 | sip line from main pipe to pou
4 | SIP_PRESSURIZE | 1 | 0 | 0 | 0 | 0 | liquid line from main pipe to pou not open pou valve
5 | CIP_CHROMA | 0 | 0 | 1 | 0 | 0 | cip chroma commad from chroma
6 | CHROMA | 0 | 1 | 0 | 0 | 0 | open pou valve
7
8
9
10
11
Notes:
a)
b)
c)

## EM_B_HCL_2 (hidden)
Table!A1
EM_B_HCL_2
Unit Class |  | 3702AV127 | 3702AV128 | 3702AV142 | 3702AV143
1-Tank CIP Skid DSP |  | X | X | X | X
Equipment Module Command | [5 empty] | Description
0 | HOLD | 0 | 0 | 0 | 0
1 | CLOSE | 0 | 0 | 0 | 0
2 | CIP_B06a | 1 | 0 | 1 | 0 | CIP B06a from cip skid
3 | CIP_B06b | 0 | 1 | 0 | 1 | CIP B06b from cip skid
4
5
6
7
8
9
10
11
Notes:
a)
b)
c)

## EM_CHROM_2 (hidden)
Table!A1
EM_CHROM_2
Unit Class | [6 empty] | Description
transfer Unit
EM_CHROM_2_7 |  | 3780AV136 | 3781AV115 | 3781AV116 | 3781AV615 | 3781AV616
EM_CHROM_2_6 |  | 3780AV129 | 3781AV117 | 3781AV118 | 3781AV617 | 3781AV618
EM_CHROM_2_5 |  | 3780AV125 | 3781AV119 | 3781AV120 | 3781AV619 | 3781AV620
EM_CHROM_2_4 |  | 3780AV122 | 3781AV121 | 3781AV122 | 3781AV621 | 3781AV622
EM_CHROM_2_3 |  | 3780AV116 | 3781AV123 | 3781AV124 | 3781AV623 | 3781AV624
EM_CHROM_2_2 |  | 3780AV110 | 3781AV125 | 3781AV126 | 3781AV625 | 3781AV626
EM_CHROM_2_1 |  | 3780AV104 | 3781AV127 | 3781AV128 | 3781AV627 | 3781AV628
Equipment Module Command
0 | HOLD | 0 | 0 | 0 | 0 | 0 | CS From source line to chrme
1 | CLOSE | 0d | 0 | 0 | 0d | 0 | CIP From source line to chrme
2 | SIP_LINE | 1 | 0 | 0 | 0 | 1 | Command from chroma to supply
3 | CIP_LINE | 1 | 0 | 0 | 1 | 0 | Command from chroma to CIP
4 | CHROM | 1 | 1 | 0 | 0 | 0 | Command from chroma to supply
5 | CIP_CHROM | 0 | 0 | 1 | 0 | 0 | Command from chroma to CIP
6 | SIP_PRESSURIZE | 1 | 0 | 0 | 0 | 0 | Pressurize after sip line
7
8
9
Notes:
a)
b)
c)

## EM_CHROM_3 (hidden)
Table!A1
EM_CHROM_3
EM_CHROM_3_1
Unit Class | [6 empty] | Description
EM_CHROM_3_7 |  | AV138 | AV129 | AV130 | AV629 | AV630
EM_CHROM_3_6 |  | AV132 | AV131 | AV132 | AV631 | AV632
EM_CHROM_3_5 |  | AV128 | AV133 | AV134 | AV633 | AV634
EM_CHROM_3_4 |  | AV124 | AV135 | AV136 | AV635 | AV636
EM_CHROM_3_3 |  | AV118 | AV137 | AV138 | AV637 | AV638
EM_CHROM_3_2 |  | AV112 | AV139 | AV140 | AV639 | AV640
EM_CHROM_3_1 |  | AV106 | AV141 | AV142 | AV641 | AV642
Equipment Module Command | [6 empty] | Description
0 | HOLD | 0 | 0 | 0 | 0 | 0 | CS From source line to chrme
1 | CLOSE | 0d | 0 | 0 | 0d | 0 | CIP From source line to chrme
2 | SIP_LINE | 1 | 0 | 0 | 0 | 1 | Command from chroma to supply
3 | CIP_LINE | 1 | 0 | 0 | 1 | 0 | Command from chroma to CIP
4 | CHROM | 1 | 1 | 0 | 0 | 0 | Command from chroma to supply
5 | CIP_CHROM | 0 | 0 | 1 | 0 | 0 | Command from chroma to CIP
6 | SIP_PRESSURIZE | 1 | 0 | 0 | 0 | 0 | Pressurize after sip line
8
9
10
Notes:
a)
b)
c)

## EM_CHROM_4 (hidden)
Table!A1
EM_CHROM_4
EM_CHROM_4_1
Unit Class | [6 empty] | Description
EM_CHROM_4_7 |  | AV137 | AV143 | AV144 | AV643 | AV644
EM_CHROM_4_6 |  | AV131 | AV145 | AV146 | AV645 | AV646
EM_CHROM_4_5 |  | AV127 | AV147 | AV148 | AV647 | AV648
EM_CHROM_4_4 |  | AV123 | AV149 | AV150 | AV649 | AV650
EM_CHROM_4_3 |  | AV117 | AV151 | AV152 | AV651 | AV652
EM_CHROM_4_2 |  | AV111 | AV153 | AV154 | AV653 | AV654
EM_CHROM_4_1 |  | AV105 | AV155 | AV156 | AV655 | AV656
Equipment Module Command
0 | HOLD | 0 | 0 | 0 | 0 | 0 | CS From source line to chrme
1 | CLOSE | 0d | 0 | 0 | 0d | 0 | CIP From source line to chrme
2 | SIP_LINE | 1 | 0 | 0 | 0 | 1 | Command from chroma to supply
3 | CIP_LINE | 1 | 0 | 0 | 1 | 0 | Command from chroma to CIP
4 | CHROM | 1 | 1 | 0 | 0 | 0 | Command from chroma to supply
5 | CIP_CHROM | 0 | 0 | 1 | 0 | 0 | Command from chroma to CIP
6 | SIP_PRESSURIZE | 1 | 0 | 0 | 0 | 0 | Pressurize after sip line
7
8
9
10
11
Notes:
a)
b)
c)

## EM_B_XFER (hidden)
EM_B_XFER
Unit Class
EM_B_XFER_10M |  | 1782AV108 | 1783AV126 | 1784AV126
EM_B_XFER_11M |  |  | 1783AV128 | 1784AV128 | 1785AV116
EM_B_XFER_20M |  |  | 1783AV124 | 1784AV124
EM_B_XFER_21M |  |  | 1783AV122 | 1784AV122 | 1785AV110
EM_B_XFER_30M |  |  | 1783AV114 | 1784AV114 | 1785AV102
EM_B_XFER_31M |  |  | 1783AV116 | 1784AV116
EM_B_XFER_32M |  |  | 1783AV118 | 1784AV118
EM_B_XFER_33M |  | 1782AV102 | 1783AV120 | 1784AV120
EM_B_XFER_40M |  |  | 1783AV106
EM_B_XFER_41M |  |  | 1783AV108
EM_B_XFER_42M |  | 1782AV104 | 1783AV110
EM_B_XFER_43M |  |  | 1783AV112
EM_B_XFER_50M |  | 1782AV106 | 1783AV102
EM_B_XFER_51M |  |  | 1783AV104
Equipment Module Command | [5 empty] | Description
0 | HOLD | 0 |  |  | 0
1 | CLOSE | 0 |  |  | 0
2 | CIP_SIP | A1 |  |  | A2 | just not for transfer phase
3 | TRANSFER | 1 |  |  | 1 | Only for transfer phase
Notes:
a) | A1: IF want to SIP/CIP CHROM2 or CHROM 3 or CHROM 4 ,then OPEN; else if transfer run, then open
b) | A2: IF want to SIP/CIP CHROM 3 or CHROM 4 ,then OPEN ; else if transfer run, then open
c)

## EM_B_CIP2_PBC_1 (hidden)
Table!A1
EM_B_CIP2_PBC_1
Unit Class |  | 3790AV962 | 3790AV963 | 3790AV964 | 3790AV965
Only EM |  | X | X | X | X
Equipment Modul Command | [5 empty] | Description
1 | HOLD | 0 | 0 | 0 | 0
2 | CLOSE | 0 | 0 | 0 | 0
3 | CIP | A1 | A2 | A3 | A4 | Choose the pipe
4
5
6
7
8
9
10
Notes:
a) | A1 IF Clean object is supply 2,then open
b) | A2 IF Clean object is supply 1,then open
c) | A3 IF Clean object is supply 2,then open
d) | A4 IF Clean object is supply 1,then open
e) | 3750/3751/37523650/3660/3661 as supply 1
f) | 3740/3741/3742/3743/3730/3731/3732/B05/B06/3860 as supply 2

## EM_B_CIP2_PBC_2 (hidden)
Table!A1
EM_B_CIP2_PBC_2
Unit Class |  | 3790AV901 | 3790AV902 | 3790AV948 | 3790AV949
Only EM |  | X | X | X | X
Equipment Modul Command | [5 empty] | Description
1 | HOLD | 0 | 0 | 0 | 0
2 | CLOSE | 0 | 0 | 0 | 0
3 | CIP | A1 | A2 | A3 | A4 | Choose the pipe
4
5
6
7
8
9
10
Notes:
a) | A1 IF cip skid is 3790,then open
b) | A2 IF cip skid is 3690,then open
c) | A3 IF cip skid is 3690,then open
d) | A4 IF cip skid is 3790,then open

## EM_TCU
EM_TCU
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | TAG5 | TAG6 | TAG7 | SYSTEM
Process Tank (DPS) |  | EM_DSXTCU01 | PV-DSXTCU0101 | PV-DSXTCU0102 | PV-DSXTCU0103 | PV-DSXTCU0104 | TV-DSXTCU0101 | TV-DSXTCU0102 | PU-DSXTCU0101 | TCU
Equipment Modul Command | [9 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | All valves closed
2 | GLW_FILL |  | 1 | 0 | 1 | 0 | 1 | 0 | 0 | Fill glycol water into pipe
3 | GLW_FILL_PU |  | 1 | 0 | 1 | 0 | 1 | 0 | 1 | Fill glycol water into pipe with pump start
4 | GLW_DR |  | 0 | 0 | 0 | 1 | 1 | 0 | 0 | Glycol water drain
5 | GLW_CIR_HEAT |  | 0 | 1 | 0 | 0 | 0 | RCAS1 | 1 | Glycol water circulation with heating
6 | GLW_CIR_TC |  | 1 | 1 | 1 | 0 | RCAS2 | RCAS2 | 1 | Glycol water circulation with temperature control
Notes:
a) | "X" in EM_DSX represents Line number. "X" can be 1, 2, 3, 4.
b) | RCAS1: increase TV-DSXTCU0102 open value if TIT_DSXTCU0101<set point-△T; decrease TV-DSXTCU0102 open value if TIT_DSXTCU0101>set pointset point+△T;
c) | RCAS2: increase TV-DSXTCU0102 open value if TIT_DSXTCU0101<set point-△T; decrease TV-DSXTCU0102 open value if TIT_DSXTCU0101>set point+△T; decrease TV-DSXTCU0101 open value if TIT_DSXTCU0101<set point-△T; increase TV-DSXTCU0101 open value if TIT_DSXTCU0101>set point+△T

## EM_PUR_PS
EM_PUR_PS
Unit Class |  | EM_NAME | TAG1 | TAG2 | SYSTEM
Process Tank (DPS) |  | EM_DSXPUR_PS | PV-DSXTCU0171 | PV-DSXTCU0170 | TCU
Equipment Modul Command |  |  |  |  | Description
0 | HOLD |  | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | All valves closed
2 | PS_SUPPLY |  | 1 | 1 | Steam supply
Notes:
a) | "X" in EM_DSX represents Line number. "X" can be 1, 2, 3, 4.