## Cover Sheet
Equipment Module (EM) Specification
EM_CHT
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. Morimatsu |  | Revision
M2 Project |  |  | PP20-0098-T-004224 |  | 1.0
| Initials | Date |  | Signature
Morimatsu prepared: | 吴婷 | 2021-03-03 |  | 吴婷
Morimatsu approved: | 张予婧 | 2021-03-03 |  | 张予婧
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Equipment Module (EM) Specification provides the description for all Equipment Module Classes to be implemented in the DeltaV DCS Software. All required Equipment Module Classes are specified in this document.
2. | Method
The Equipment Module (EM) Specification is subdivided into two sections for the a Physical Part and for the Procedural Part.
The section for the Physical Part identifies the Unit Classes which will use the Equipment Module Class, and all Devices that are part of the Equipment Module. The Spread Sheet identifies by X all Devices that belong to the Equipment Module. Devices are all used actuators and PID control loops.
For valves the following informations are added to the Tag name, if applicable: NO
| NO | Valves with "normaly open" state
| FB | Valves with physical feedback signal
The section for the Procedural Part specifies all required Equipment Module Commands in a matrix which shows the activation of the individual devices per EM Command. The following keys are used for identification of the control state of the devices:
| 0 | Valve closed (also for NO valves), Motor/Pump stopped
| 1 | Valve open (also for NO valves), Motor/Pump running
| 0d | Valve closes with delay, Motor/Pump stops with delay
| 1d | Valve opens with delay, Motor/Pump starts with delay
| c | Valve/Motor/Pump controlled by PID control loop
| p | Valve pulsed
| RCAS | PID control loop operates in closed loop mode with setpoint from phase
| ROUT | PID control loop operates in open loop mode with direct control of output from phase
3. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| EM | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | EM_TOP_VALVES_1
| EM-Command | max. 16 characters, capital letters, _ for delimiter |  |  | SIP_XFER_OUT
4. | Change Log
The Equipment Module Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done only if Equipment Module Classes are added or deleted, and for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-31 | 吴婷
| 0.1a | 2020-11-09 | 吴婷 | EM_CHT_CIP_IN中阀门位号修改，EM_CHT_BUF_IN阀门位号修改
| 0.1b | 2020-11-18 | 吴婷 | EM_CHT_BUF_IN移除三个EM，加入到EM_CHT_CIP当中;
| 0.1c | 2020-11-20 | 吴婷 | EM_CHT_BUF_IN添加A1,A2两个逻辑
| 1.0 | 2021-03-03 | 吴婷 | 根据程序仿真和水试修改

## Table
NO | Original name | Changed name
1 | EM_CHT_PD_IN
2 | EM_CHT_PD_OUT
3 | EM_CHT_BUF_IN
4 | EM_CHT_DRN
5 | EM_CHT_CIP
6 | EM_CHT_CIP_IN
7 | EM_CHT_BRK

## EM_CHT_PD_IN
EM_CHT_PD_IN
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | SYSTEM
HPLC #1 WORK UNIT CHT01 |  | EM_DSXCHT01_PDIN | N/A | PV-DSXCHT0105 | PV-DSXCHT0106 | PV-DSXCHT0107 | Purification System
HPLC #2 WORK UNIT CHT02 |  | EM_DSXCHT02_PDIN | PV-DSXCHT0243 | PV-DSXCHT0201 | PV-DSXCHT0202 | PV-DSXCHT0203
HPLC #3 WORK UNIT CHT03 |  | EM_DSXCHT03_PDIN | PV-DSXCHT0302 | PV-DSXCHT0303 | PV-DSXCHT0304 | PV-DSXCHT0305
Equipment Module Command | [6 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | All valves closed
2 | CHT_CIP |  | 0 | 0 | 1 | 1 | CH CIP
3 | PD_IN |  | 1 | 1 | 1 | 0 | Product into CH
4 | PD_IN_MIXER |  | 0 | 1 | 1 | 0 | Product (from mixer) into CH, only for CHT02&CHT03
5 | PD_IN_CIP |  | 1 | 1 | 0 | 1 | Product transfer pipe CIP
6 | PD_IN_SIP |  | 1 | 1 | 0 | 1 | Product transfer pipe SIP
7 | PD_IN_DRN |  | 1 | 1 | 0 | 1 | Product transfer pipe Drain
8 | PD_IN_PR |  | 1 | 1 | 0 | 0 | Keep prussure for Product transfer pipe
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.

## EM_CHT_PD_OUT
EM_CHT_PD_OUT
|  |  | CH OUT | CIPS/CS | PD TO a | CC
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | SYSTEM
HPLC #1 WORK UNIT CHT01 |  | EM_DSXCHT01PDOUT | PV-DSXCHT0144 | PV-DSXCHT0143 | PV-DSXCHT0140 | PV-DSXCHT0141 | Purification System
HPLC #2 WORK UNIT CHT02 |  | EM_DSXCHT02PDOUT | PV-DSXCHT0227 | PV-DSXCHT0228 | PV-DSXCHT0229 | PV-DSXCHT0230
HPLC #3 WORK UNIT CHT03 |  | EM_DSXCHT03PDOUT | PV-DSXCHT0329 | PV-DSXCHT0330 | PV-DSXCHT0331 | PV-DSXCHT0332
Equipment Module Command | [6 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | All valves closed
2 | PD_OUT |  | 1 | 0 | 1 | 0 | Product to tank
3 | PD_OUT_CIP |  | 1 | 1 | 1 | 0 | Product transfer line CIP
4 | PD_OUT_SIP |  | 1 | 1 | 1 | 1 | Product transfer line SIP
5 | PD_OUT_DRN |  | 1 | 0 | 1 | 1 | Product transfer line drain
6 | PD_OUT_CIP_DRN |  | 1 | 1 | 1 | p1 | Product transfer line CIP pulse drain
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.

## EM_CHT_BUF_IN
EM_CHT_BUF_IN
|  |  | BUF IN | IN CHT | CIP | BUF DIS | BUF TA16 DIS
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | TAG5 | SYSTEM
HPLC #1 WORK UNIT CHT01 |  | EM_DSXCHT01TA18 | PV-DSXCHT0117 | PV-DSXCHT0118 | PV-DSXCHT0119 | N/A | N/A | Purification System
HPLC #1 WORK UNIT CHT01 |  | EM_DSXCHT01TA19 | PV-DSXCHT0120 | PV-DSXCHT0121 | PV-DSXCHT0122 | N/A | N/A
HPLC #1 WORK UNIT CHT01 |  | EM_DSXCHT01TA34 | PV-DSXCHT0131 | PV-DSXCHT0132 | PV-DSXCHT0133 | PV-DSXTA3407 | N/A
HPLC #1 WORK UNIT CHT01 |  | EM_DSXCHT01TA33 | PV-DSXCHT0134 | PV-DSXCHT0135 | PV-DSXCHT0136 | PV-DSXTA3204 | PV-DSXTA1624
HPLC #1 WORK UNIT CHT01 |  | EM_DSXCHT01TA27 | PV-DSXCHT0137 | PV-DSXCHT0139 | PV-DSXCHT0138 | N/A | N/A
HPLC #1 WORK UNIT CHT01 |  | EM_DSXCHT01TA17 | PV-DSXCHT0114 | PV-DSXCHT0115 | PV-DSXCHT0116 | N/A | N/A
HPLC #2 WORK UNIT CHT02 |  | EM_DSXCHT02TA34 | PV-DSXCHT0213 | PV-DSXCHT0214 | PV-DSXCHT0215 | PV-DSXTA3408 | N/A
HPLC #2 WORK UNIT CHT02 |  | EM_DSXCHT02TA28 | PV-DSXCHT0216 | PV-DSXCHT0217 | PV-DSXCHT0218 | N/A | N/A
HPLC #2 WORK UNIT CHT02 |  | EM_DSXCHT02TA22 | PV-DSXCHT0232 | PV-DSXCHT0233 | PV-DSXCHT0234 | PV-DSXTA2212 | N/A
HPLC #2 WORK UNIT CHT02 |  | EM_DSXCHT02TA29 | PV-DSXCHT0235 | PV-DSXCHT0236 | PV-DSXCHT0237 | PV-DSXTA2813 | N/A
HPLC #3 WORK UNIT CHT03 |  | EM_DSXCHT03TA35 | PV-DSXCHT0315 | PV-DSXCHT0316 | PV-DSXCHT0317 | PV-DSXTA3416 | N/A
HPLC #3 WORK UNIT CHT03 |  | EM_DSXCHT03TA23 | PV-DSXCHT0318 | PV-DSXCHT0319 | PV-DSXCHT0320 | N/A | N/A
HPLC #3 WORK UNIT CHT03 |  | EM_DSXCHT03TA22 | PV-DSXCHT0336 | PV-DSXCHT0337 | PV-DSXCHT0338 | PV-DSXTA2211 | N/A
HPLC #3 WORK UNIT CHT03 |  | EM_DSXCHT03TA24 | PV-DSXCHT0339 | PV-DSXCHT0340 | PV-DSXCHT0341 | PV-DSXTA2218 | N/A
Description
0 | HOLD |  | 0 | 0 | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | 0 | All valves closed
2 | BUF_IN |  | 1 | 1 | 0 | A3 | A4 | Buffer into CHT
3 | BUF_IN_CIP |  | 1 | 0 | 1 | A1 | A2 | Buffer transfer pipe CIP
4 | CHT_CIP |  | 0 | 1 | 1 | 0 | 0 | CH CIP
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.
b) | A1: IF THISUNIT="TA16 ", THEN CLOSE; IF THISUNIT="OTHERS", THEN OPEN
c) | A2: IF THISUNIT="TA16 ", THEN OPEN; IF THISUNIT="OTHERS", THEN CLOSE
A3: IF PH_X_BH_CHT="Phase:TA16_TO_CHT01 ", THEN CLOSE; IF THISUNIT="OTHERS", THEN OPEN
A4: IF PH_X_BH_CHT="Phase:TA16_TO_CHT01 ", THEN OPEN; IF THISUNIT="OTHERS", THEN CLOSE
Note on G24: 作者: 1改为A1

## EM_CHT_DRN
EM_CHT_DRN
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | TAG5 | TAG6 | SYSTEM
HPLC #1 WORK UNIT CHT01 |  | EM_DSXCHT01_DRN | PV-DSXCHT0142 | PV-DSXCHT0145 | PV-DSXTA0291 | PV-DSXCHT0128 | PV-DSXCHT0129 | PV-DSXCHT0130 | Purification System
HPLC #2 WORK UNIT CHT02 |  | EM_DSXCHT02_DRN | PV-DSXCHT0222 | PV-DSXCHT0223 | PV-DSXTA0487 | PV-DSXCHT0224 | PV-DSXCHT0225 | PV-DSXCHT0226
HPLC #3 WORK UNIT CHT03 |  | EM_DSXCHT03_DRN | PV-DSXCHT0324 | PV-DSXCHT0326 | PV-DSXTA0587 | PV-DSXCHT0325 | PV-DSXCHT0327 | PV-DSXCHT0328
Equipment Module Command | [8 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | 0 | 0 | All valves closed
2 | PE_DRN |  | 1 | 0 | 0 | 1 | 1 | 0 | Pipe drain
3 | PE_PUL_DRN |  | 1 | 0 | 0 | 1 | p1 | 0 | Pipe drain by pulse
4 | PE_SIP |  | 1 | 0 | 0 | 1 | 0 | 1 | Pipe SIP
5 | PE_SIP_BPS |  | 1 | 0 | 0 | 1 | 1 | 1 | Pipe SIP bypass
6 | PE_CIPR |  | 1 | 1 | 1 | 0 | 0 | 0 | Pipe CIPR
7 | PE_CIPR_PUL_DRN |  | 1 | 1 | 1 | 1 | p1 | 0 | Pipe CIPR drain by pulse
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.
b) | p1: pulse open 10s, and closes 20s. Parameter can be modified in EM.

## EM_CHT_CIP
EM_CHT_CIP
|  |  | NaOH/WFI IN | IN CHT | CIP
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | SYSTEM
HPLC #1 WORK UNIT CHT01 |  | EM_DSXCHT01CIPAL | PV-DSXCHT0125 | PV-DSXCHT0127 | PV-DSXCHT0126 | Purification System
HPLC #1 WORK UNIT CHT01 |  | EM_DSXCHT01CIPW | PV-DSXCHT0111 | PV-DSXCHT0112 | PV-DSXCHT0113
HPLC #1 WORK UNIT CHT01 |  | EM_DSXCHT01CIPST | PV-DSXCHT0108 | PV-DSXCHT0109 | PV-DSXCHT0110
HPLC #2 WORK UNIT CHT02 |  | EM_DSXCHT02CIPAL | PV-DSXCHT0210 | PV-DSXCHT0211 | PV-DSXCHT0212
HPLC #2 WORK UNIT CHT02 |  | EM_DSXCHT02CIPW | PV-DSXCHT0207 | PV-DSXCHT0208 | PV-DSXCHT0209
HPLC #2 WORK UNIT CHT02 |  | EM_DSXCHT02CIPST | PV-DSXCHT0204 | PV-DSXCHT0205 | PV-DSXCHT0206
HPLC #3 WORK UNIT CHT03 |  | EM_DSXCHT03CIPAL | PV-DSXCHT0312 | PV-DSXCHT0313 | PV-DSXCHT0314
HPLC #3 WORK UNIT CHT03 |  | EM_DSXCHT03CIPW | PV-DSXCHT0309 | PV-DSXCHT0310 | PV-DSXCHT0311
HPLC #3 WORK UNIT CHT03 |  | EM_DSXCHT03CIPST | PV-DSXCHT0306 | PV-DSXCHT0307 | PV-DSXCHT0308
Equipment Module Command | [5 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | All valves closed
2 | ALW_IN |  | 1 | 1 | 0 | NaOH or WFI into CH
3 | ALW_IN_PUL |  | 1 | p1 | 0 | WFI into CH by pulse
4 | ALW_IN_CIP |  | 1 | 0 | 1 | NaOH/WFI transfer pipe CIP
5 | CHT_CIP |  | 0 | 1 | 1 | CHT CIP
6 | ALL IN |  | 1 | 1 | 1 | NaOH or WFI into CHT to clean valves
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.
b) | p1: tag 3 close 10s and then open 20s

## EM_CHT_CIP_IN
EM_CHT_CIP_IN
Unit Class |  | EM_NAME | TAG1 | TAG2 | SYSTEM
HPLC #1 WORK UNIT CHT01 |  | EM_DSXCHT01CIPIN | PV-DSXCHT0146 | PV-DSXTA0282 | Purification System
HPLC #2 WORK UNIT CHT02 |  | EM_DSXCHT02CIPIN | PV-DSXCHT0241 | PV-DSXTA0488
HPLC #3 WORK UNIT CHT03 |  | EM_DSXCHT03CIPIN | PV-DSXCHT0342 | PV-DSXTA0582
Equipment Module Command |  |  |  |  | Description
0 | HOLD |  | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | All valves closed
2 | CIP_IN |  | 1 | 0 | CIP transfer line of WFI or NaOH
3 | CS_IN |  | 1 | 1 | SIP transfer line of WFI or NaOH
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.

## EM_CHT_BRK
EM_CHT_BRK
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | SYSTEM
HPLC #1 WORK UNIT CHT01 |  | EM_DSXCHT01_BRK | PV-DSXCHT0124 | PV-DSXCHT0147 | PV-DSXCHT0148 | PV-DSXCHT0149 | Purification System
HPLC #2 WORK UNIT CHT02 |  | EM_DSXCHT02_BRK | PV-DSXCHT0242 | PV-DSXCHT0247 | PV-DSXCHT0248 | PV-DSXCHT0249
HPLC #3 WORK UNIT CHT03 |  | EM_DSXCHT03_BRK | PV-DSXCHT0343 | PV-DSXCHT0347 | PV-DSXCHT0348 | PV-DSXCHT0349
Equipment Module Command | [6 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | All valves closed
2 | PD_PE_CIP |  | 1 | 0 | 0 | 0 | Product transfer pipe CIP
3 | PD_PE_SIP |  | 1 | 1 | 0 | 1 | Product transfer pipe SIP
4 | BUF_CIP_DRN |  | 0 | p1 | 1 | 0 | Buffer transfer pipe CIP pulse drain
5 | BUF_SIP_HEAT |  | 0 | 1 | 1 | 0 | Buffer transfer pipe SIP pre-heat
6 | BUF_SIP |  | 0 | 1 | 0 | 1 | Buffer transfer pipe SIP
7 | PD_SIP_HEAT |  | 1 | 1 | 1 | 0 | Product transfer pipe SIP pre-heat
8 | PD_CIP_DRN |  | 1 | p1 | 1 | 0 | Product transfer pipe CIP pulse drain
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.
b) | p1: pulse open ,10s, then closes 20s. Parameter can be modified in EM.
|  |  |  | 新增 | 新增 | 新增