## Cover Sheet
Equipment Module (EM) Specification
EM_DF
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. Morimatsu |  | Revision
M2 Project |  |  | PP20-0098-T-004225 |  | 1.0
| Initials | Date |  | Signature
Morimatsu prepared: | 吴婷 | 2021-03-03 |  | 吴婷
Morimatsu approved: | 张予婧 | 2021-03-03 |  | 张予婧
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Equipment Module (EM) Specification provides the description for all Equipment Module Classes to be implemented in the DeltaV DCS Software. All required Equipment Module Classes are specified in this document.
2. | Method
The Equipment Module (EM) Specification is subdivided into two sections for the a Physical Part and for the Procedural Part.
The section for the Physical Part identifies the Unit Classes which will use the Equipment Module Class, and all Devices that are part of the Equipment Module. The Spread Sheet identifies by X all Devices that belong to the Equipment Module. Devices are all used actuators and PID control loops.
For valves the following informations are added to the Tag name, if applicable: NO
| NO | Valves with "normaly open" state
| FB | Valves with physical feedback signal
The section for the Procedural Part specifies all required Equipment Module Commands in a matrix which shows the activation of the individual devices per EM Command. The following keys are used for identification of the control state of the devices:
| 0 | Valve closed (also for NO valves), Motor/Pump stopped
| 1 | Valve open (also for NO valves), Motor/Pump running
| 0d | Valve closes with delay, Motor/Pump stops with delay
| 1d | Valve opens with delay, Motor/Pump starts with delay
| c | Valve/Motor/Pump controlled by PID control loop
| p | Valve pulsed
| RCAS | PID control loop operates in closed loop mode with setpoint from phase
| ROUT | PID control loop operates in open loop mode with direct control of output from phase
3. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| EM | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | EM_TOP_VALVES_1
| EM-Command | max. 16 characters, capital letters, _ for delimiter |  |  | SIP_XFER_OUT
4. | Change Log
The Equipment Module Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done only if Equipment Module Classes are added or deleted, and for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-31 | 吴婷
| 0.1a | 2020-11-18 | 吴婷 | EM_DF03修改TAG7的开关状态，修改TAG10控制逻辑
| 1.0 | 2021-03-03 | 吴婷 | 根据程序仿真和水试修改

## Table
NO | Original name | Changed name
1 | EM_DF03
2 | EM_DF03_FILT

## EM_DF03
EM_DF03
|  |  | PD-TA03 | WFI-TA20 | BF-TA21 | BF-TA34 | BF/WFI | WFI反洗隔断 | FCV | BF-TA21 DIS | BF-TA34 DIS | PU | DR
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | TAG5 | TAG6 | TAG7 | TAG8 | TAG9 | TAG10 | TAG11 | TAG12 | SYSTEM
Depth Filtration Unit DF03 |  | EM_DSXDF03 | PV-DSXDF0301 | PV-DSXDF0314 | PV-DSXDF0316 | PV-DSXDF0317 | PV-DSXDF0302 | PV-DSXDF0315 | FCV-DSXDF0301 | PV-DSXTA2105 | PV-DSXTA3409 | PU-DS1DF0301 | PV-DSXDF0303 | FIC-DSXDF0301 | Purification System
Equipment Module Command | [14 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | All valves closed
2 | PD_IN_PU |  | 1 | 0 | 0 | 0 | 0 | 0 | SP% | 0 | 0 | PID+RCAS | 0 | FIC SP= FT_SP | Product into DF with pump start
3 | WFI_FR_TA20_PU |  | 0 | 1 | 0 | 0 | 1 | 1 | SP% | 0 | 0 | PID+RCAS | 0 | FIC SP=FT_SP | WFI from TA20 into DF with pump start
4 | BUF_FR_TA21_PU |  | 0 | 0 | 1 | 0 | 1 | 1 | SP% | 1 | 0 |  | 0 |  | Buffer from TA21 into DF with pump start
5 | BUF_FR_TA34_PU |  | 0 | 0 | 0 | 1 | 1 | 0 | SP% | 0 | 1 |  | 0 |  | Buffer from TA34 into DFwith pump start
6 | PD_IN |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | Product into DF without pump start | only used when blow
7 | WFI_FR_TA20 |  | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 |  | WFI from TA20 into DF without pump start
8 | BUF_FR_TA21 |  | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 |  | Buffer from TA21 into DF without pump start
9 | BUF_FR_TA34 |  | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 0 |  | Buffer from TA34 into DFwithout pump start
10 | PD_IN_DRN |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 |  | Product Pipe from drain
11 | WFI_FR_TA20_DRN |  | 0 | 1 | 0 | i | 1 | 1 | 1 | 0 | 0 | 0 | 1 |  | Pipe from TA20 drain
12 | BUF_FR_TA21_DRN |  | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 1 |  | Pipe from TA21 drain
13 | BUF_FR_TA34_DRN |  | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 |  | Pipe from TA34 drain
14 | WFI_CIP |  | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | WFI in for CIP | 反洗
15 | PD_IN_SIP |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 |  | SIP of Product in pipe
16 | BUF_FR_TA21_SPD |  | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | PID+ROUT | 0 | FIC OUT=PU_SPD | CIP from TA21 to DF with pump start
17 | BUF_FR_TA34_SPD |  | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | PID+ROUT | 0 | FIC OUT=PU_SPD | CIP from TA34 to DF with pump start
18 | PD_IN_SPD |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | PID+ROUT | 0 | FIC OUT=PU_SPD | CIP from TA03 to DF with pump start
19 | WFI_FR_TA20_SPD |  | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | PID+ROUT | 0 | FIC OUT=PU_SPD | WFI from TA20 into DF with pump start when vent
20 | PD_FR_PT01_PU |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PID+RCAS | 0 | FIC SP= FT_SP | Product from PT01 into DF with pump start
21 | PD_FR_PT01_SPD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PID+ROUT | 0 | FIC OUT=PU_SPD | Product from PT01 into DF with pump start when vent
Notes:
a) | TAG10 with PID control to reach TAG11 set point FT_SP which is set in phase.
b) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.
c) | For command 16/17/18, LCS-PUDS1DF03_01 state=1 and last for 5sec then start the PUMP | bar: TAG1 to TAG4

## EM_DF03_FILT
EM_DF03_FILT
PD OUT
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | TAG5 | TAG6 | TAG7 | TAG8 | TAG9 | SYSTEM
Depth Filtration Unit DF03 |  | EM_FDSXDF0301 | PV-DSXDF0304 | PV-DSXDF0309 | PV-DSXDF0305 | PV-DSXDF0306 | PV-DSXDF0310 | PV-DSXDF0311 | PV-DSXDF0312 | PV-DSXDF0313 | PV-DSXDF0308 | Purification System
Equipment Module Command | [11 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | All valves closed
2 | PD_TS1 |  | 1 | A1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | Product transfer with LS control | X_BH_DF
3 | PD_TS2 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | Product transfer
4 | PD_TS3 |  | 1 | p1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | Product transfer to vent | X_BH_DF
5 | PE_CIP |  | 1 | p3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | CIP product transfer pipe
6 | PE_SIP |  | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | SIP filter
7 | BUF_IN_CIP |  | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | Buffer transfer line CIP
8 | PD_DRN |  | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | Drain after product transfer
9 | BUF_DRN |  | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | Buffer drain when rinse depth filter
10 | PUL_DRN |  | 1 | 0 | p2 | p2 | 1 | 0 | 1 | 0 | 1 | Drain when CIP
11 | PE_SIP_HEAT | [10 empty] | Heat transfer line when SIP | bar: TAG1 to PD OUT TAG9
12 | BUF_IN_SIP |  | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | Buffer transfer line SIP
13 | BUF_IN_SIP_BPS |  | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | Buffer transfer line SIP bypass
14 | BLOW_DRN |  | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | Blow drain depth filter
15 | PE_SIP_COOL |  | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | Cool down after SIP
16 | PE_PR |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | Keep purssure for pipe after SIP
Notes:
a) | p1: open TAG2 5s, then close. Parameter can be modified in EM.
b) | p2: pulse both open TAG3 and TAG4 together 5s, close 15s. Parameter can be modified in EM.
c) | p3: pulse both TAG2 10s, close 10s. Parameter can be modified in EM.
d) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.
e) | A1: when LS-DSXDF0301=0,open,when LS-DSXDF0301=1,close