## Cover Sheet
Equipment Module (EM) Specification
EM_PUR
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. Morimatsu |  | Revision
M2 Project |  |  | PP20-0098-T-004226 |  | 1.0
| Initials | Date |  | Signature
Morimatsu prepared: | 吴婷 | 2021-03-03 |  | 吴婷
Morimatsu approved: | 张予婧 | 2021-03-03 |  | 张予婧
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Equipment Module (EM) Specification provides the description for all Equipment Module Classes to be implemented in the DeltaV DCS Software. All required Equipment Module Classes are specified in this document.
2. | Method
The Equipment Module (EM) Specification is subdivided into two sections for the a Physical Part and for the Procedural Part.
The section for the Physical Part identifies the Unit Classes which will use the Equipment Module Class, and all Devices that are part of the Equipment Module. The Spread Sheet identifies by X all Devices that belong to the Equipment Module. Devices are all used actuators and PID control loops.
For valves the following informations are added to the Tag name, if applicable: NO
| NO | Valves with "normaly open" state
| FB | Valves with physical feedback signal
The section for the Procedural Part specifies all required Equipment Module Commands in a matrix which shows the activation of the individual devices per EM Command. The following keys are used for identification of the control state of the devices:
| 0 | Valve closed (also for NO valves), Motor/Pump stopped
| 1 | Valve open (also for NO valves), Motor/Pump running
| 0d | Valve closes with delay, Motor/Pump stops with delay
| 1d | Valve opens with delay, Motor/Pump starts with delay
| c | Valve/Motor/Pump controlled by PID control loop
| p | Valve pulsed
| RCAS | PID control loop operates in closed loop mode with setpoint from phase
| ROUT | PID control loop operates in open loop mode with direct control of output from phase
3. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| EM | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | EM_TOP_VALVES_1
| EM-Command | max. 16 characters, capital letters, _ for delimiter |  |  | SIP_XFER_OUT
4. | Change Log
The Equipment Module Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done only if Equipment Module Classes are added or deleted, and for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-31 | 吴婷
| 0.1a | 2020-11-09 | 吴婷 | EM_PUR_HEAD, EM_PUR_PD_OUT,EM_PUR_PA,EM_PUR_CIPR部分位号及命名修改
| 0.1b | 2020-11-18 | 吴婷 | EM_PUR_BOM增加一条command,三个阀门从TAG4移除，新建一个TAG; EM_PUR_HEAD新增一个阀门，修改个别阀门开关状态
| 0.1c | 2020-11-20 | 吴婷 | EM_PUR_HEAD, EM_PUR_PD_OUT修改
| 0.1d | 2020-12-10 | 吴婷 | EM_PUR_BOM中位号修改；EM_PUR_HEAD逻辑修改，EM_PUR_TOP中SIP_TPK逻辑修改
| 1.0 | 2021-03-03 | 吴婷 | 根据程序仿真修改

## Table
NO | Original name | Changed name
1 | EM_PUR_PD_IN
2 | EM_PUR_FA1
3 | EM_PUR_FA2
4 | EM_PUR_FA3
5 | EM_PUR_TOP
6 | EM_PUR_HEAD
7 | EM_PUR_BOM
8 | EM_PUR_JC
9 | EM_PUR_PD_OUT
10 | EM_PUR_CS
11 | EM_PUR_PA
12 | EM_PUR_CIPS1
13 | EM_PUR_CIPS2
14 | EM_PUR_CIPR
15 | EM_PUR_CIPR_PU

## EM_PUR_PD_IN
EM_PUR_PD_IN
|  |  | BUF DIS | BUF | WFI | RE CIP | BUF+WFI | PD1 | PD2 | BUF+PD
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | TAG5 | TAG6 | TAG7 | TAG8 | SYSTEM
4000L PURIFICATION TANK UNIT TA03 |  | EM_DSXTA03_PD_IN | PV-DSXTA2106 | PV-DSXTA0382C | PV-DSXTA0383C | PV-DSXTA0375C | PV-DSXTA0372C | PV-DSXTA0373C | N/A | N/A | Purification System
4000L PURIFICATION TANK UNIT TA04 |  | EM_DSXTA04_PD_IN | PV-DSXTA2814 | PV-DSXTA0483C | PV-DSXTA0482C | PV-DSXTA0475C | PV-DSXTA0409D | PV-DSXTA0410D | N/A | N/A
4000L PURIFICATION TANK UNIT TA05 |  | EM_DSXTA05_PD_IN | PV-DSXTA3415 | PV-DSXTA0507A | N/A | N/A | N/A | PV-DSXTA0508A | N/A | N/A
3000L PURIFICATION TANK UNIT TA06 |  | EM_DSXTA06_PD_IN | PV-DSXTA3022 | PV-DSXTA0670E | N/A | N/A | N/A | PV-DSXTA0671E | PV-DSXTA0628E | PV-DSXTA0627E
Equipment Modul Command | [10 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | All valves closed
2 | WFI_TO_TK |  | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | WFI into tank,only for TA03&TA04
3 | BUF_TO_TK |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | Buffer into tank
4 | PD1_TO_TK |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | Product 1 into tank
5 | PD2_TO_TK |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Product 2 into tank,only for TA06
6 | CIP_PE_WFI |  | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | CIP transfer pipe of WFI,only for TA03&TA04 | 反洗
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.

## EM_PUR_FA1
EM_PUR_FA1
|  |  | F_to TA | F_to DRN | PA PE_to DRN | PA From | VENT
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | TAG5 | SYSTEM
4000L PURIFICATION TANK UNIT TA03 | 4000L PURIFICATION TANK UNIT TA03 | EM_DSXTA03_FA | PV-DS1TA0320C | PV-DS1TA0353C | PV-DS1TA0358C | PV-DS1TA0352C | PV-DS1TA0351C | Purification System
4000L PURIFICATION TANK UNIT TA04 | 4000L PURIFICATION TANK UNIT TA04 | EM_DSXTA04_FA | PV-DS1TA0420D | PV-DS1TA0453D | PV-DS1TA0458D | PV-DS1TA0452D | PV-DS1TA0451D
4000L PURIFICATION TANK UNIT TA05 | 4000L PURIFICATION TANK UNIT TA05 | EM_DSXTA05_FA | PV-DS1TA0520A | PV-DS1TA0553A | PV-DS1TA0558A | PV-DS1TA0552A | PV-DS1TA0551A
3000L PURIFICATION TANK UNIT TA06 | 3000L PURIFICATION TANK UNIT TA06 | EM_DSXTA06_FA | PV-DS1TA0620E | PV-DS1TA0653E | PV-DS1TA0658E | PV-DS1TA0652E | PV-DS1TA0651E
3000L PURIFICATION TANK UNIT TA08 | 3000L PURIFICATION TANK UNIT TA08 | EM_DSXTA08_FA | PV-DS1TA0820F | PV-DS1TA0853F | PV-DS1TA0858F | PV-DS1TA0852F | PV-DS1TA0851F
Equipment Modul Command | [7 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | 0 | All valves closed
2 | PRESSURE_CONT |  | 1 | 0 | 0 | A1 | A2 | Tank pressure control
3 | VENT_FA |  | 1 | 0 | 0 | 0 | 1 | Vent to atmosphere
4 | SIP_FA |  | 1 | 1 | 1 | 0 | 0 | SIP filter
5 | PA_TK |  | 1 | 0 | 0 | 1 | 0 | Pressure air into tank for transferring product | 压料时使用
6 | PA_TK_DRN1 |  | 1 | 1 | p2 | 0 | 0 | Pressure air into tank after SIP,for TA03~06 | 蒸汽与无菌压空在源头合并，用于SIP后破真空,适用于TA03~06
7 | PA_TK_DRN2 |  | 1 | 1 | p2 | 1 | 0 | Pressure air into tank after SIP,oniy for TA08 | 适用于TA08
8 | AT_TK |  | 1 | 0 | 0 | 0 | 0 | Air test for tank.
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.
b) | A1: if PIT01* ＜SP - △P, TAG4 open, when PIT01*≥SP, TAG4 close
c) | A2: if PIT01* ＞SP + △P, TAG5 open, when PIT01*≤ SP, TAG5 close
d) | p2: pulse open TAG2 5s, then close15s. Parameter can be modified in EM.

## EM_PUR_FA2
EM_PUR_FA2
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | TAG5 | TAG6 | SYSTEM
4000L Harvest Tank Unit TA02 |  | EM_DSXTA02_FA1 | PV-DSXTA0235 | PV-DSXTA0244 | PV-DSXTA0234 | PV-DSXTA0236 | PV-DSXTA0268 | PV-DSXTA0279
Equipment Modul Command | [8 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | 0 | 0 | All valves closed
2 | PRESSURE_CONT |  | 1 | 0 | A2 | A1 | 0 | 0 | Tank pressure control
3 | VENT_FA |  | 1 | 0 | 1 | 0 | 0 | 0 | Vent to atmosphere
4 | SIP_FA |  | 0 | 1 | 0 | 0 | 1 | 1 | SIP filter
5 | PA_TK |  | 1 | 0 | 0 | 1 | 0 | 0 | Pressure air into tank for transferring product | 压料时使用
6 | PW_ALK_FA |  | 0 | 0 | 0 | 0 | 0 | p1 | CIP tank with alkali or PW
7 | WFI_PA_FA |  | 0 | p2 | 0 | 0 | 0 | p1 | CIP tank with WFI or PA
8 | PA_TK_DRN |  | 0 | p2 | 0 | 0 | 1 | 1 | Pressure air into tank after SIP
9 | AT_TK |  | 0 | 0 | 0 | 0 | 0 | 0 | Air test for tank.
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.
b) | A1: if PIT01* ＜ SP - △P, TAG4 open, when PIT01*≥SP, TAG4 close
c) | A2: if PIT01* ＞ SP + △P, TAG3 open, when PIT01*≤ SP, TAG3 close
d) | p1: pulse close TAG6 30s, open 10s. Parameter can be modified in EM.
e) | p2: pulse open TAG3 5s, then close15s. Parameter can be modified in EM.

## EM_PUR_FA3
EM_PUR_FA3
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | TAG5 | TAG6 | SYSTEM
4000L Harvest Tank Unit TA02 |  | EM_DSXTA02_FA2 | PV-DSXTA0210 | PV-DSXTA0211 | PV-DSXTA0237 | PV-DSXTA0238 | PV-DSXTA0245 | FIT-DSXTA0201
Equipment Modul Command | [8 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | 0 | 0 | All valves closed
2 | SIP_FA |  | 1 | 1 | 0 | 0 | 1 | 0 | SIP filter
3 | WFI_PA_FA |  | p2 | 1 | 0 | 0 | p1 | 0 | CIP filter with WFI or PA
4 | PA_TK |  | 0 | 1 | 1 | 1 | 0 | FIC OUT = SP1 | Pressure air into tank when product storage in the tank
5 | PW_ALK_FA |  | p2 | 1 | 0 | 0 | 0 | 0 | CIP filter with PW or Alkali
6 | PA_TK_DRN |  | 1 | 1 | 0 | 0 | p3 | 0 | Pressure air into tank after SIP | 蒸汽与无菌压空在源头合并，用于SIP后破真空
7 | AT_TK |  | 0 | 1 | 0 | 0 | 0 | 0 | Air test for FA
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.
b) | p1: pulse open TAG5 5s, then close15s. Parameter can be modified in EM.
c) | p2: pulse close TAG1 30s, open 10s. Parameter can be modified in EM.
d) | p3: pulse open TAG3 5s, then close15s. Parameter can be modified in EM.

## EM_PUR_TOP
EM_PUR_TOP
|  |  | PD in | PD to TK | PD to TK | CIP in | CIP Return1 | CIP Return2 | SIP Drain | PD TK inlet | J tube | SPRAY 1 | SPRAY 2 | PD inlet drain | PD inlet drain
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | TAG5 | TAG6 | TAG7 | TAG8 | TAG9 | TAG10 | TAG11 | TAG12 | TAG13 | SYSTEM
4000L HARVEST TANK UNIT TA02 |  | EM_DSXTA02_TOP | N/A | PV-DSXTA0202 | N/A | PV-DSXTA0209 | N/A | N/A | N/A | PV-DSXTA0206 | PV-DSXTA0272 | PV-DSXTA0204 | PV-DSXTA0205 | N/A | N/A
4000L PURIFICATION TANK UNIT TA03 |  | EM_DSXTA03_TOP | PV-DSXTA0305C | PV-DSXTA0303C | PV-DSXTA0301C | PV-DSXTA0306C | PV-DSXTA0304C | PV-DSXTA0339 | PV-DSXTA0302C | PV-DSXTA0307C | PV-DSXTA0380 | PV-DSXTA0317C | PV-DSXTA0318C | PV-DSXTA0356C | PV-DSXTA0357C | Purification System
4000L PURIFICATION TANK UNIT TA04 |  | EM_DSXTA04_TOP | PV-DSXTA0405D | PV-DSXTA0403D | PV-DSXTA0401D | PV-DSXTA0406D | PV-DSXTA0404D | PV-DSXTA0437 | PV-DSXTA0402D | PV-DSXTA0407D | PV-DSXTA0480 | PV-DSXTA0417D | PV-DSXTA0418D | PV-DSXTA0456D | PV-DSXTA0457D
4000L PURIFICATION TANK UNIT TA05 |  | EM_DSXTA05_TOP | PV-DSXTA0505A | PV-DSXTA0503A | PV-DSXTA0501A | PV-DSXTA0506A | PV-DSXTA0504A | PV-DSXTA0543 | PV-DSXTA0502A | PV-DSXTA0509A | PV-DSXTA0580 | PV-DSXTA0517A | PV-DSXTA0518A | PV-DSXTA0556A | PV-DSXTA0557A
3000L PURIFICATION TANK UNIT TA06 |  | EM_DSXTA06_TOP | PV-DSXTA0605E | PV-DSXTA0603E | PV-DSXTA0601E | PV-DSXTA0606E | PV-DSXTA0604E | PV-DSXTA0633 | PV-DSXTA0602E | PV-DSXTA0607E | PV-DSXTA0680 | PV-DSXTA0617E | PV-DSXTA0618E | PV-DSXTA0656E | PV-DSXTA0657E
3000L PURIFICATION TANK UNIT TA08 |  | EM_DSXTA08_TOP | PV-DSXTA0805F | PV-DSXTA0801F | PV-DSXTA0856F | PV-DSXTA0806F | N/A | N/A | PV-DSXTA0880F | PV-DSXTA0803F | PV-DSXTA0882F | PV-DSXTA0817F | PV-DSXTA0818F | PV-DSXTA0881F | PV-DSXTA0857F
Equipment Module Command | [15 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | All valves closed
2 | PD_IN |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | Product/Buffer in tank
3 | CIP_TK |  | 0 | 1 | 1 | 1 | 0 | 0 | 0 | p1 | p4 | p2 | p3 | 0 | 0 | CIP supply to spray balls and J tube
4 | CIP_IN |  | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | CWFI supply to tank
5 | CIP_PD_IN_PE1 |  | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CIP supply to Product inlet pipe,only for TA02~06
6 | CIP_PD_IN_PE2 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CIP supply to Product inlet pipe,only for TA08 | 反洗
7 | CIP_BUF_IN_PE |  | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | CIP supply to Buffer inlet pipe
8 | SIP_TK |  | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | SIP Tank
9 | SIP_PD_IN_PE1 |  | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | SIP supply to Product/Buffer inlet pipe，only for TA03~06，TA08
10 | SIP_PD_IN_PE2 |  | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | SIP supply to Product inlet pipe，only for TA02 | 只适用于TA02
11 | SIP_TKP |  | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | SIP tank and pipe
12 | SIP_PD_IN_BPS1 |  | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | SIP Product/Buffer inlet pipe bypass，only for TA03~06，TA08
13 | SIP_PD_IN_BPS2 |  | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | SIP Product inlet pipe bypass，only for TA02 | 只适用于TA02
14 | PD_IN_DRN1 |  | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | Product/Buffer inlet pipe drain,only for TA03~06,TA08
15 | PD_IN_DRN2 |  | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | Product inlet pipe drain,only for TA02 | 只适用于TA02
16 | PD_IN_PUL |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | p5 | 0 | 0 | 0 | 0 | 0 | Product/Buffer in tank by pulse
17 | PD_IN_PUL_DRN |  | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | p6 | 0 | Product/Buffer inlet pipe drain by pulse，only for TA03~06
18 | PD_IN_AT |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Air test of product/Buffer inlet pipe
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.
b) | p1/2/3/4: pulse open TAG8 and TAG9 for 7s, then close 3s, TAG9, TAG10 for 17s, then close 3s. Parameter can be modified in EM.
c) | p5: pulse open TAG7, open for 3s,then close7s. Parameter can be modified in EM.
d) | p6: pulse open TAG10, open for 10s,then close20s. Parameter can be modified in EM.

## EM_PUR_HEAD
EM_PUR_HEAD
|  |  | CIP in | CS in | to CHT02/03 | to TK | to P | to TK | to TK | to filter | to UF01/P | to filter | to CHT01 | to P | to TK
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | TAG5 | TAG6 | TAG7 | TAG8 | TAG9 | TAG10 | TAG11 | TAG12 | TAG13 | SYSTEM
3000L BUFFER PREPARATION TANK UNIT TA12 |  | EM_DSXTA12_HEADER | PV-DSXTA1204C | PV-DSXTA1203C |  |  | PV-DSXTA1206C | PV-DSXTA1203C | N/A | N/A |  | N/A | N/A |  |  | Buffer Preparation System
3000L BUFFER PREPARATION TANK UNIT TA13 |  | EM_DSXTA13_HEADER | PV-DSXTA1304B | PV-DSXTA1303B |  |  | PV-DSXTA1306B | PV-DSXTA1303B | N/A | N/A |  | N/A | N/A
6000L BUFFER PREPARATION TANK UNIT TA14 |  | EM_DSXTA14_HEADER | PV-DSXTA1404C | PV-DSXTA1403C |  |  | PV-DSXTA1406C | PV-DSXTA1403C | N/A | N/A |  | N/A | N/A
9000L BUFFER PREPARATION TANK UNIT TA15 |  | EM_DSXTA15_HEADER | PV-DSXTA1508B | PV-DSXTA1503B |  |  | PV-DSXTA1506B | PV-DSXTA1503B | N/A | N/A |  | N/A | N/A
3000L BUFFER HOLDING TANK UNIT TA16 |  | EM_DSXTA16_HEADER | PV-DSXTA1608A | PV-DSXTA1610A |  |  | PV-DSXTA1611A | PV-DSXTA1612A | N/A | N/A |  | N/A | N/A |  |  | Buffer Holding System
3000L BUFFER HOLDING TANK UNIT TA17 |  | EM_DSXTA17_HEADER | PV-DSXTA1708A | PV-DSXTA1710A |  |  | PV-DSXTA1711A | PV-DSXTA1712A | N/A | N/A |  | N/A | N/A
3000L BUFFER HOLDING TANK UNIT TA18 |  | EM_DSXTA18_HEADER | PV-DSXTA1808B | PV-DSXTA1810B |  |  | PV-DSXTA1811B | PV-DSXTA1812B | N/A | N/A |  | N/A | N/A
3000L BUFFER HOLDING TANK UNIT TA19 |  | EM_DSXTA19_HEADER | PV-DSXTA1908B | PV-DSXTA1910B |  |  | PV-DSXTA1911B | PV-DSXTA1912B | N/A | N/A |  | N/A | N/A
3000L PROCESS WATER TANK UNIT TA20 |  | EM_DSXTA20_HEADER | PV-DSXTA2008A | PV-DSXTA2010A |  |  | PV-DSXTA2011A | PV-DSXTA2012A | N/A | N/A |  | N/A | N/A
3000L BUFFER HOLDING TANK UNIT TA21 |  | EM_DSXTA21_HEADER | PV-DSXTA2108A | PV-DSXTA2110A |  |  | PV-DSXTA2111A | PV-DSXTA2112A | N/A | N/A |  | N/A | N/A
3000L BUFFER HOLDING TANK UNIT TA22 |  | EM_DSXTA22_HEADER | PV-DSXTA2208A | PV-DSXTA2210A |  |  | PV-DSXTA2211A | PV-DSXTA2212A | N/A | N/A |  | N/A | N/A
3000L BUFFER HOLDING TANK UNIT TA23 |  | EM_DSXTA23_HEADER | PV-DSXTA2308B | PV-DSXTA2310B |  |  | PV-DSXTA2311B | PV-DSXTA2312B | N/A | N/A |  | N/A | N/A
3000L BUFFER HOLDING TANK UNIT TA24 |  | EM_DSXTA24_HEADER | PV-DSXTA2408B | PV-DSXTA2410B |  |  | PV-DSXTA2411B | PV-DSXTA2412B | N/A | N/A |  | N/A | N/A
6000L BUFFER HOLDING TANK UNIT TA26 |  | EM_DSXTA26_HEADER | PV-DSXTA2608A | PV-DSXTA2610A |  |  | PV-DSXTA2611A | PV-DSXTA2612A | N/A | N/A |  | N/A | N/A
6000L BUFFER HOLDING TANK UNIT TA27 |  | EM_DSXTA27_HEADER | PV-DSXTA2708B | PV-DSXTA2710B |  |  | PV-DSXTA2711B | PV-DSXTA2712B | N/A | N/A |  | N/A | N/A
6000L BUFFER HOLDING TANK UNIT TA28 |  | EM_DSXTA28_HEADER | PV-DSXTA2808A | PV-DSXTA2810A |  |  | PV-DSXTA2811A | PV-DSXTA2812A | N/A | N/A |  | N/A | N/A
6000L BUFFER HOLDING TANK UNIT TA29 |  | EM_DSXTA29_HEADER | PV-DSXTA2908B | PV-DSXTA2910B |  |  | PV-DSXTA2911B | PV-DSXTA2912B | N/A | N/A |  | N/A | N/A
3000L BUFFER HOLDING TANK UNIT TA30 |  | EM_DSXTA30_HEADER | PV-DSXTA3008A | PV-DSXTA3010A |  |  | PV-DSXTA3011A | PV-DSXTA3012A | N/A | N/A |  | N/A | N/A
6000L BUFFER HOLDING TANK UNIT TA31 |  | EM_DSXTA31_HEADER | PV-DSXTA3108A | PV-DSXTA3110A |  |  | PV-DSXTA3111A | PV-DSXTA3112A | N/A | N/A |  | N/A | N/A
9000L 0.5M NaOH TANK UNIT TA32 |  | EM_DSXTA32_HEADER | PV-DSXTA3208A | PV-DSXTA3210A |  |  | PV-DSXTA3211A | PV-DSXTA3212A | N/A | N/A |  | N/A | N/A
9000L BUFFER HOLDING TANK UNIT TA33 |  | EM_DSXTA33_HEADER | PV-DSXTA3308B | PV-DSXTA3310B |  |  | PV-DSXTA3311B | PV-DSXTA3312B | N/A | N/A |  | N/A | N/A
9000L BUFFER HOLDING TANK UNIT TA34 |  | EM_DSXTA34_HEADER | PV-DSXTA3408A | PV-DSXTA3410A |  |  | PV-DSXTA3411A | PV-DSXTA3412A | N/A | N/A |  | N/A | N/A
9000L BUFFER HOLDING TANK UNIT TA35 |  | EM_DSXTA35_HEADER | PV-DSXTA3508B | PV-DSXTA3510B |  |  | PV-DSXTA3511B | PV-DSXTA3512B | N/A | N/A |  | N/A | N/A
4000L HARVEST TANK UNIT TA02 |  | EM_DSXTA02_HEAD | PV-DSXTA0271 | PV-DSXTA0233 | N/A | N/A | PV-DSXTA0207 | PV-DSXTA0220 | PV-DSXTA0249 | PV-DSXTA0239 | N/A | PV-DSXTA0226 | PV-DSXTA0227 | N/A | N/A | Purification System
4000L PURIFICATION TANK UNIT TA03 |  | EM_DSXTA03_HEAD | PV-DSXTA0313C | PV-DSXTA0312C | N/A | N/A | PV-DSXTA0316C | PV-DSXTA0315C | N/A | N/A | N/A | N/A | N/A | N/A | N/A
4000L PURIFICATION TANK UNIT TA04 |  | EM_DSXTA04_HEAD | PV-DSXTA0413D | PV-DSXTA0412D | PV-DSXTA0427 | PV-DSXTA0426 | PV-DSXTA0416D | PV-DSXTA0415D | N/A | N/A | N/A | N/A | N/A | N/A | N/A
4000L PURIFICATION TANK UNIT TA05 |  | EM_DSXTA05_HEAD | PV-DSXTA0513A | PV-DSXTA0512A | PV-DSXTA0527 | PV-DSXTA0526 | PV-DSXTA0516A | PV-DSXTA0515A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
3000L PURIFICATION TANK UNIT TA06 |  | EM_DSXTA06_HEAD | PV-DSXTA0613E | PV-DSXTA0612E | N/A | N/A | PV-DSXTA0616E | PV-DSXTA0615E | N/A | N/A | N/A | N/A | N/A | N/A | N/A
3000L PURIFICATION TANK UNIT TA08 |  | EM_DSXTA08_HEAD | PV-DSXTA0813F | PV-DSXTA0812F | N/A | N/A | N/A | PV-DSXTA0885 | PV-DSXTA0871 | N/A | PV-DSXTA0870 | N/A | N/A | PV-DSXTA0816F | PV-DSXTA0888
Equipment Module Command | [15 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | All valves closed
2 | CIP_TK |  | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | CIP supply to spray balls, J tube,filter
3 | CIP_IN |  | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | CWFI supply to tank
4 | CIP_NF |  | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | CIP supply to NF，only for TA08 | 反洗
5 | CIP_UF |  | 1 | 0 | 0 | 0 | 0 | A1 | 0 | 0 | A1 | 0 | 0 | 0 | 0 | CIP supply to UF
6 | CIP_PE |  | 1 | 0 | 0 | A2 | A2 | A3 | 0 | 0 | A3 | 0 | 0 | A3 | 0 | CIP supply to tank outlet pipe
7 | CIP_CHT_OUT |  | 1 | 0 | A4 | 0 | 0 | A5 | 0 | A5 | 0 | 0 | A5 | 0 | 0 | CIP supply to chromatography outlet pipe
8 | SIP_TK |  | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | SIP tank
9 | SIP_PE |  | 0 | 1 | 0 | A2 | A2 | A3 | 0 | 0 | A3 | 0 | 0 | A3 | 0 | SIP tank outlet pipe
10 | SIP_TKP |  | 0 | 1 | 0 | A2 | A2 | 1 | 1 | A2 | A3 | A2 | 0 | A3 | 1 | SIP tank and pipe
11 | SIP_CHT_OUT |  | 0 | 1 | A4 | 0 | 0 | A5 | 0 | A5 | 0 | 0 | A5 | 0 | 0 | SIP chromatography outlet pipe
12 | SIP_UF |  | 0 | 1 | 0 | 0 | 0 | A6 | 0 | 0 | A6 | 0 | 0 | 0 | 0 | SIP supply to UF
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.
b) | A1:IF THISUNIT="UF01" Then OPEN;IF THISUNIT="others" Then CLOSE;
A2:IF THISUNIT=TA02~TA06 ,DF03,NF01Then OPEN;IF THISUNIT="others" Then CLOSE;
A3:IF THISUNIT=TA02~TA06 ,DF03,NF01 Then CLOSE;IF THISUNIT="others" Then OPEN;
A4:IF THISUNIT=CHT02 0r CHT03 Then OPEN,IF THISUNIT="others" Then CLOSE;
A5:IF THISUNIT=CHT02 0r CHT03 Then CLOSE,IF THISUNIT="others" Then OPEN;
A6:IF THISUNIT="UF01" of line 1/3，Then OPEN;IF THISUNIT="UF01" of line 2/4，Then CLOSE;IF THISUNIT="UF02" Then CLOSE;

## EM_PUR_BOM
EM_PUR_BOM
|  |  | TK BOM | P BOM | PD OUT | CIPR | DR+CC | CIPR |  | DR | CC | CIPR+DR
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | TAG5 | TAG6 | TAG7 | TAG8 | TAG9 | TAG10 | SYSTEM
4000L HARVEST TANK UNIT TA02 |  | EM_DSXTA02_BOM | PV-DSXTA0214 | PV-DSXTA0213 | PV-DSXTA0216 | PV-DSXTA0215 | PV-DSXTA0217 | N/A | PV-DSXTA0284 | PV-DSXTA0241 | PV-DSXTA0242 | N/A | Purification System
4000L PURIFICATION TANK UNIT TA03 |  | EM_DSXTA03_BOM | PV-DSXTA0321C | PV-DSXTA0322C | PV-DSXTA0323C | PV-DSXTA0324C | PV-DSXTA0325C | PV-DSXTA0332 | PV-DSXTA0384 | PV-DSXTA0354C | PV-DSXTA0355C | N/A
4000L PURIFICATION TANK UNIT TA04 |  | EM_DSXTA04_BOM | PV-DSXTA0421D | PV-DSXTA0422D | PV-DSXTA0423D | PV-DSXTA0424D | PV-DSXTA0425D | PV-DSXTA0428 | PV-DSXTA0484 | PV-DSXTA0454D | PV-DSXTA0455D | N/A
4000L PURIFICATION TANK UNIT TA05 |  | EM_DSXTA05_BOM | PV-DSXTA0521A | PV-DSXTA0523A | PV-DSXTA0522A | N/A | PV-DSXTA0525A | PV-DSXTA0530 | PV-DSXTA0528A | PV-DSXTA0554A | PV-DSXTA0555A | PV-DSXTA0524A
3000L PURIFICATION TANK UNIT TA06 |  | EM_DSXTA06_BOM | PV-DSXTA0621E | PV-DSXTA0623E | PV-DSXTA0622E | N/A | PV-DSXTA0625E | PV-DSXTA0630 | PV-DSXTA0626E | PV-DSXTA0654E | PV-DSXTA0655E | PV-DSXTA0624E
3000L PURIFICATION TANK UNIT TA08 |  | EM_DSXTA08_BOM | PV-DSXTA0821F | PV-DSXTA0823F | PV-DSXTA0822F | N/A | PV-DSXTA0825F | PV-DSXTA0884 | PV-DSXTA0828F | PV-DSXTA0854F | PV-DSXTA0855F | PV-DSXTA0824F
Equipment Module Command | [12 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | All valves closed
2 | PD_OUT |  | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Transfer product from tank to target
3 | TK_DRN |  | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | Empty tank to closed drain
4 | CIP_TK |  | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | CIP return from bottom valve to CIPR line
5 | CIP_PE |  | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CIP transfer pipe and cool
6 | CIP_PE_PUL_DRN |  | 0 | 1 | 1 | 0 | p1 | 0 | 0 | 1 | 0 | 1 | CIP transfer pipe，only used when PA blow
7 | CIP_UF_TK |  | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | CIP transfer pipe from UF to TA05 or TA08 | 反洗
8 | CIP_NF_TK |  | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | CIP transfer pipe from NF to TA05 or TA06 | 反洗
9 | SIP_TK_HEAT |  | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | Heat Tank
10 | SIP_TK |  | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | SIP Tank
11 | SIP_PE_HEAT |  | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | Heat pipe
12 | SIP_PE |  | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | SIP transfer pipe
13 | SIP_TKP_HEAT |  | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | Heat tank and pipe
14 | SIP_TKP |  | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | SIP tank and pipe
15 | SIP_PUL_DRN |  | 1 | 0 | 0 | 0 | 1 | 0 | 1 | p2 | 1 | 1 | Pulse drain when SIP
16 | AT |  | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Air test
17 | PR_PE |  | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Keep puessure for pipe after SIP
18 | PR_TKP |  | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Keep puessure for tank and pipe after SIP
19 | CHT_VT |  | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | CHT product inlet pipe vent
20 | CIP_UF_TK_DRN |  | 0 | 0 | 1 | 1 | p3 | 1 | 0 | 1 | 0 | 1
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.
b) | p1: pulse open ,10s, then closes 20s. Parameter can be modified in EM.
c) | p2: pulse open TAG8,10s, then closes 10s. Parameter can be modified in EM.

## EM_PUR_PD_OUT
EM_PUR_PD_OUT
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | SYSTEM
4000L Purification Holding Unit TA05 |  | EM_DSXTA05_PDOUT | PV-DSXTA0570 | PV-DSXTA0571 | PV-DSXTA0573 | PV-DSXTA0572 | Purification System
3000L Purification Holding Unit TA08 |  | EM_DSXTA08_PDOUT | N/A | PV-DSXTA0886 | PV-DSXTA0887 | N/A
3000L Purification Holding Unit TA06 |  | EM_DSXTA06_PDOUT | N/A | PV-DSXTA0673 | PV-DSXTA0674 | N/A
Equipment Modul Command | [6 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | All valves closed
2 | PD_OUT1 |  | 0 | 1 | 0 | 1 | Product from TA05 to NF01/Product from TA08 to UF02 /Product from TA06 to NF01
3 | PD_OUT2 |  | 0 | 0 | 1 | 0 | Product from TA05 to UF01，only for DS1TA05./Product from TA08 to TA06 /Product from TA06 to UF01
4 | PD_OUT3 |  | 1 | 1 | 0 | 0 | Product from TA05 to CHT03
Notes:
a) | "X" in "DSX" represents Line number. "X" can be1, 2, 3, 4.
b) | TAG2&TAG3 of TA05&TA06 are only applied in DS1&DS3.

## EM_PUR_JC
EM_PUR_JC
|  |  | CC | TCM out | PS in | PA in | GLWR | TCM in | GLWS | RTN | DR
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | TAG5 | TAG6 | TAG7 | TAG8 | TAG9 | SYSTEM
4000L HARVEST TANK UNIT TA02 |  | EM_DSXTA02_JC | PV-DS1TA0240 | PV-DS1TA0263A | PV-DS1TA0260A | PV-DS1TA0262A | PV-DS1TA0261A | PV-DS1TA0264C | PV-DS1TA0264A | PV-DS1TA0265A | PV-DS1TA0267 | Purification System
4000L PURIFICATION TANK UNIT TA03 |  | EM_DSXTA03_JC | PV-DS1TA0369C | PV-DS1TA0360C | PV-DS1TA0361C | PV-DS1TA0362C | PV-DS1TA0363C | PV-DS1TA0364C | PV-DS1TA0365C | PV-DS1TA0366C | PV-DS1TA0368C
4000L PURIFICATION TANK UNIT TA04 |  | EM_DSXTA04_JC | PV-DS1TA0469D | PV-DS1TA0460D | PV-DS1TA0461D | PV-DS1TA0462D | PV-DS1TA0463D | PV-DS1TA0464D | PV-DS1TA0465D | PV-DS1TA0466D | PV-DS1TA0468D
4000L PURIFICATION TANK UNIT TA05 |  | EM_DSXTA05_JC | PV-DS1TA0569A | PV-DS1TA0560A | PV-DS1TA0561A | PV-DS1TA0562A | PV-DS1TA0563A | PV-DS1TA0564A | PV-DS1TA0565A | PV-DS1TA0566A | PV-DS1TA0568A
3000L PURIFICATION TANK UNIT TA06 |  | EM_DSXTA06_JC | PV-DS1TA0669E | PV-DS1TA0660E | PV-DS1TA0661E | PV-DS1TA0662E | PV-DS1TA0663E | PV-DS1TA0664E | PV-DS1TA0665E | PV-DS1TA0666E | PV-DS1TA0668E
3000L PURIFICATION TANK UNIT TA08 |  | EM_DSXTA08_JC | PV-DS1TA0869F | PV-DS1TA0860F | PV-DS1TA0861E | PV-DS1TA0862F | PV-DS1TA0863F | PV-DS1TA0864F | PV-DS1TA0865F | PV-DS1TA0866F | PV-DS1TA0867F
Equipment Module Command | [11 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | All valves closed
2 | JC_BW_BK |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | Pressure air blow GLW back to returen main pipe
3 | TEMP_CONT |  | 0 | 0 | 0 | 0 | A1 | 0 | A1 | 0 | 0 | Cooling the media with GLW
4 | JC_COOL |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | Coling tank after SIP with TCM water
5 | JC_COOL_PUL |  | 0 | 0 | 0 | 0 | 1 | 0 | p1 | 0 | 0 | Coling tank after SIP with TCM water by pulse
6 | JC_HEAT |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | Heating jacket while tank SIP
7 | JC_DRN |  | 0 | 0 | 0 | d1 | 0 | 0 | 0 | 0 | 1 | Drain jacket
8 | JC_GLW_HEAT |  | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Glycol water heating jacket
Notes:
a) | "X" in EM_DSX represents Line number. "X" can be 1, 2, 3, 4.
b) | d1: open TAG4 with delay 5s. Parameter can be modified in EM.
c) | A1: if TT ＜ SP-ΔT, TAG5 and TAG7close, when TT ＞ SP+ΔT,TAG5 and TAG7 open
d) | p1: pulse open TAG6 10s, then closes 5s. Parameter can be modified in EM.

## EM_PUR_CS
EM_PUR_CS
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 |  | SYSTEM
Purification System |  | EM_DSXPUR_CS1 | PV-DSXTA0230 | PV-DSXTA0672 | PCV-DSXTA0201 | PIC-DSXTA0205 |  | Purification System
Purification System |  | EM_DSXPUR_CS2 | PV-DSXTA0831 | PV-DSXTA0873 | PCV-DSXTA0801 | PIC-DSXTA0802
Equipment Module Command | [7 empty] | Description
0 | HOLD |  | 0 | 0 | 0 |  |  | Hold state
1 | CLOSE |  | 0 | 0 | 0 |  |  | All valves closed
2 | CS_SUPPLY |  | 1 | 1 | c | RCAS | PIC OUT | Steam Supply
Notes:
a) | "X" in "DSX" represents Line number. "X" can be1, 2, 3, 4.
b) | c: TAG3 with PID control to reach TAG4 set point.

## EM_PUR_PA
EM_PUR_PA
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | TAG5 | SYSTEM
Purification System |  | EM_DSXPUR_PA | PV-DSXTA0289 | PV-DSXTA0285 | PV-DSXTA0286 | PV-DSXTA0287 | PV-DSXTA0290 | Purification System
Equipment Module Command | [7 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | 0 | All valves closed
2 | PA_PE |  | 1 | 0 | 1 | 0 | 0 | Pressure air into pipe after SIP
3 | SIP_FA |  | 0 | 1 | 0 | 1 | 1 | SIP filter
4 | PA_FA |  | 1 | 1 | 0 | 1 | 0 | Pressure air into filter after SIP
Notes:
a) | "X" in "DSX" represents Line number. "X" can be1, 2, 3, 4.
b) | d1: open TAG4 with delay 30s. Parameter can be modified in EM.

## EM_PUR_CIPS1
EM_PUR_CIPS1
|  |  | TA03 or CHT01 | TA03 | CHT01 | TA04 | TA05 or CHT02 | TA05 | CHT02 | TA06 or CHT03 | TA06 | CHT03 | TA07 or UF01 | TA07 | UF01 | UF01
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | TAG5 | TAG6 | TAG7 | TAG8 | TAG9 | TAG10 | TAG11 | TAG12 | TAG13 | TAG14 | SYSTEM
Purification room utility 纯化间公用 |  | EM_DSXPUR_CIPS1 | PV-DSXTA0232 | PV-DSXTA0280 | PV-DSXTA0281 | PV-DSXTA0314C | PV-DSXTA0414D | PV-DSXTA0485 | PV-DSXTA0481 | PV-DSXTA0514A | PV-DSXTA0585 | PV-DSXTA0581 | PV-DSXTA0687 | PV-DSXTA0685 | PV-DSXTA0681 | PV-DSYUF0101 | Purification System
Equipment Modul | [16 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | All valves closed
2 | CIP_TO_TA03 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CIP_TO_TA03
3 | CIP_TO_CHT01 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CIP_TO_CHT01
4 | CIP_TO_TA04 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CIP_TO_TA04
5 | CIP_TO_TA05 |  | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CIP_TO_TA05
6 | CIP_TO_CHT02 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CIP_TO_CHT02
7 | CIP_TO_TA06 |  | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | CIP_TO_TA06
8 | CIP_TO_CHT03 |  | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | CIP_TO_CHT03
9 | CIP_TO_TA07 |  | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | CIP_TO_TA07
10 | CIP_TO_UF01 |  | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | CIP_TO_UF01
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.
"Y" in "DSY" represents Line number. "Y" can be 1, 3.

## EM_PUR_CIPS2
EM_PUR_CIPS2
|  |  | UF02 | UF01 | UF01
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | SYSTEM
Purification room utility 纯化间公用 |  | EM_DSXPUR_CIPS2 | PV-DSXTA0883 | PV-DSXTA0815F | PV-DSYUF0102 | Purification System
Equipment Modul Command | [5 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | All valves closed
2 | CIP_TO_UF01 |  | 0 | 1 | 1 | CIP_TO_UF01
3 | CIP_TO_UF02 |  | 1 | 0 | 0 | CIP_TO_UF02
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.
"Y" in "DSY" represents Line number. "Y" can be 1, 3.

## EM_PUR_CIPR
EM_PUR_CIPR
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | TAG5 | TAG6 | TAG7 | TAG8 | TAG9 | TAG10 | TAG11 | TAG12 | SYSTEM
Purification System公用 |  | EM_DSXPUR_CIPR | PV-DSXTA0292 | PV-DSXTA0338 | PV-DSXTA0333 | PV-DSXTA0436 | PV-DSXTA0429 | PV-DSXTA0486 | PV-DSXTA0542 | PV-DSXTA0531 | PV-DSXTA0586 | PV-DSXTA0632 | PV-DSXTA0631 | PV-DSXTA0686 | Purification System
Equipment Module Command | [14 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | All valves closed
2 | CIPR_FR_TA02 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | CIP return from TA02
3 | CIPR_FR_CHT01 |  | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | CIP return from CHT01
4 | CIPR_FR_TA03_IN |  | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | CIP return from TA03 inlet pipe
5 | CIPR_FR_TA03 |  | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | CIP return from TA03
6 | CIPR_FR_TA04_IN |  | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | CIP return from TA04 inlet pipe
7 | CIPR_FR_TA04 |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | CIP return from TA04
8 | CIPR_FR_CHT02 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | CIP return from CHT02
9 | CIPR_FR_TA05_IN |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | CIP return from TA05 inlet pipe
10 | CIPR_FR_TA05 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | CIP return from TA05
11 | CIPR_FR_CHT03 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | CIP return from CHT03
12 | CIPR_FR_TA06_IN |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | CIP return from TA06 inlet pipe
13 | CIPR_FR_TA06 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | CIP return from TA06
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.

## EM_PUR_CIPR_PU
EM_PUR_CIPR_PU
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 |  | SYSTEM
Purification System公用 |  | EM_DSXPUR1CIPRPU | PV-DSXTA0647 | PV-DSXTA0648 | PU-DSXTA0601 |  | Purification System
Purification System公用 |  | EM_DSXPUR2CIPRPU | PV-DSXTA0847 | PV-DSXTA0848 | PU-DS1TA0801
Equipment Module Command | [6 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | All valves closed
2 | PU_ON |  | 0 | 0 | A1 | ROUT | Alkali or PW return from tank with pump Operator select pump in recipe before phase running
3 | PU_ON_DRN |  | p1 | p1 | A1 | ROUT | WFI return from tank with pump Operator select pump in recipe before phase running
4 | PU_OFF_DRN |  | p1 | p1 | 0 | 0 | Drain without pump
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.
b) | p1: pulse both open TAG1 and TAG2 together 20s, close 0s. Parameter can be modified in EM.
c) | A1：When FS01=1 and last for 10s, then PU on, when FS01=0 and last for 3s, then PU off.
d) | Pump speed control via VFD to reach set point