## Cover Sheet
Equipment Module (EM) Specification
EM_DSF
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. Morimatsu |  | Revision
M2 Project |  |  | PP20-0098-T-009981 |  | 1.0
| Initials | Date |  | Signature
Morimatsu prepared: | 吴婷 | 2021-03-03 |  | 吴婷
Morimatsu approved: | 张予婧 | 2021-03-03 |  | 张予婧
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Equipment Module (EM) Specification provides the description for all Equipment Module Classes to be implemented in the DeltaV DCS Software. All required Equipment Module Classes are specified in this document.
2. | Method
The Equipment Module (EM) Specification is subdivided into two sections for the a Physical Part and for the Procedural Part.
The section for the Physical Part identifies the Unit Classes which will use the Equipment Module Class, and all Devices that are part of the Equipment Module. The Spread Sheet identifies by X all Devices that belong to the Equipment Module. Devices are all used actuators and PID control loops.
For valves the following informations are added to the Tag name, if applicable: NO
| NO | Valves with "normaly open" state
| FB | Valves with physical feedback signal
The section for the Procedural Part specifies all required Equipment Module Commands in a matrix which shows the activation of the individual devices per EM Command. The following keys are used for identification of the control state of the devices:
| 0 | Valve closed (also for NO valves), Motor/Pump stopped
| 1 | Valve open (also for NO valves), Motor/Pump running
| 0d | Valve closes with delay, Motor/Pump stops with delay
| 1d | Valve opens with delay, Motor/Pump starts with delay
| c | Valve/Motor/Pump controlled by PID control loop
| p | Valve pulsed
| RCAS | PID control loop operates in closed loop mode with setpoint from phase
| ROUT | PID control loop operates in open loop mode with direct control of output from phase
3. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| EM | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | EM_TOP_VALVES_1
| EM-Command | max. 16 characters, capital letters, _ for delimiter |  |  | SIP_XFER_OUT
4. | Change Log
The Equipment Module Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done only if Equipment Module Classes are added or deleted, and for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-12-10 | 吴婷
| 1.0 | 2021-03-03 | 吴婷 | 根据程序仿真和水试修改

## Table
NO | Original name | Changed name
1 | EM_DSF

## EM_DSF
EM_DSF
|  |  | SC1 | SC2 | SC3 | SC4 | PU
Unit Class |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | TAG5 | SYSTEM
Slurry Tank匀浆罐 |  | EM_DSXPT07 | PV-DSXPT0704 | PV-DSXPT0701 | PV-DSXPT0702 | PV-DSXPT0703 | PU-DS1PT0701 | Purification System
Equipment Modul Command | [7 empty] | Description
0 | HOLD |  | 0 | 0 | 0 | 0 | 0 | Hold state
1 | CLOSE |  | 0 | 0 | 0 | 0 | 0 | All valves closed
2 | FILL |  | A4 | A1 | A2 | A3 | ROUT | Fill one bag with pump on
3 | FILL_ALL |  | 1 | 1 | 1 | 1 | 0 | Fill all bags without pump on
4
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.
b) | A1:IF R_SELECT_SCALE is A Then OPEN;IF R_SELECT_SCALE is others Then CLOSE;R_SELECT_SCALE is set in Phase
A2:IF R_SELECT_SCALE is B Then OPEN;IF R_SELECT_SCALE is others Then CLOSE;R_SELECT_SCALE is set in Phase
A3:IF R_SELECT_SCALE is C Then OPEN;IF R_SELECT_SCALE is others Then CLOSE;R_SELECT_SCALE is set in Phase
A4:IF R_SELECT_SCALE is D Then OPEN;IF R_SELECT_SCALE is others Then CLOSE;R_SELECT_SCALE is set in Phase