## Cover Sheet
Equipment Module (EM) Specification
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. Morimatsu |  | Revision
M2b Project |  |  | 信达M2 FS_CIPstation_EM_C_ALK |  | 1.0
| Initials | Date |  | Signature
Morimatsu prepared: | 张雨然 | 2021-03-03 |  | 张雨然
Morimatsu approved: | 张旭 | 2021-03-03 |  | 张旭
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Equipment Module (EM) Specification provides the description for all Equipment Module Classes to be implemented in the DeltaV DCS Software. All required Equipment Module Classes are specified in this document.
2. | Method
The Equipment Module (EM) Specification is subdivided into two sections for the a Physical Part and for the Procedural Part.
The section for the Physical Part identifies the Unit Classes which will use the Equipment Module Class, and all Devices that are part of the Equipment Module. The Spread Sheet identifies by X all Devices that belong to the Equipment Module. Devices are all used actuators and PID control loops.
For valves the following informations are added to the Tag name, if applicable: NO
| NO | Valves with "normaly open" state
| FB | Valves with physical feedback signal
The section for the Procedural Part specifies all required Equipment Module Commands in a matrix which shows the activation of the individual devices per EM Command. The following keys are used for identification of the control state of the devices:
| 0 | Valve closed (also for NO valves), Motor/Pump stopped
| 1 | Valve open (also for NO valves), Motor/Pump running
| 0d | Valve closes with delay, Motor/Pump stops with delay
| 1d | Valve opens with delay, Motor/Pump starts with delay
| c | Valve/Motor/Pump controlled by PID control loop
| p | Valve pulsed
| RCAS | PID control loop operates in closed loop mode with setpoint from phase
| ROUT | PID control loop operates in open loop mode with direct control of output from phase
3. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| EM | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | EM_TOP_VALVES_1
| EM-Command | max. 16 characters, capital letters, _ for delimiter |  |  | SIP_XFER_OUT
4. | Change Log
The Equipment Module Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done only if Equipment Module Classes are added or deleted, and for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-09-21 | Zhang Yuran | Draft for review
| 0.1 | 2020-11-18 | Zhang Yuran | Update for programming
| 0.1a | 2020-11-27 | Zhang Yuran | Update for programming
| 0.1b | 2020-12-07 | Zhang Yuran | Update for programming
| 1 | 2021-03-03 | Zhang Yuran | Update for SFAT

## Table
NO | Original name | Description | Rev | Name | Date
1 | EM_C_ALK | Used for Alkali tank program | 1 | Zhang Yuran | 20200921

## EM_C_ALK
EM_C_ALK
UNIT |  | EM_NAME | TAG1 | TAG2 | TAG3 | TAG4 | TAG5 | TAG6 | TAG7 | TAG8 | TAG9 | TAG10 | TAG11 | TAG12 | TAG13 | TAG14 | TAG15 | TAG16 | TAG17 |  | TAG18 | TAG19 |  | SYSTEM
Alkali Tank |  | EM_C_ALK | PV-ALK01 | PV-ALK02 | PV-ALK03 | PV-ALK04 | PV-ALK05 | PV-ALK06 | PV-ALK07 | PV-ALK08 | PV-ALK09 | PV-ALK10 | PV-ALK11 | PV-ALK26 | PV-ALK39 | PV-ALK40 | PV-ALK41 | PV-ALK45 | PU-ALK02 | SIC-01 | PV-ALK50 | AG-ALK01
Control Module Command |  | Description | PV-ALK01 | PV-ALK02 | PV-ALK03 | PV-ALK04 | PV-ALK05 | PV-ALK06 | PV-ALK07 | PV-ALK08 | PV-ALK09 | PV-ALK10 | PV-ALK11 | PV-ALK26 | PV-ALK39 | PV-ALK40 | PV-ALK41 | PV-ALK45 | PU-ALK02 | SIC-01 | PV-ALK50 | AG-ALK01 |  | Actions
1 | HOLD | Hold state | 0 | 0 | 0 | 0 | 0 | A1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | sp=0 | 0 | 0 | sp=0 | MSG0: Stop pump and then close valves. MSG1: Release all related devices. Disable all ForceSP&HM&SM A1:Open VLV_DELAY_TM, then close
2 | STOP | Stop state | 0 | 0 | 0 | 0 | 0 | A1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | sp=0 | 0 | 0 | sp=0 | MSG0: Stop pump and then close valves. MSG1: Release all related devices. Disable all ForceSP&HM&SM A1:Open VLV_DELAY_TM, then close
3 | CYCLE | Alklai tank self cycle | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A1 | SP1 | 0 | 1 | A2 | MSG0: Alkali is cycling. MSG1: Wait for CIP skid request. A1:Set SP1= PU_CIR_SPD. Delay PU_DELAY_TM, then start A2:Set agitator speed = AG_SPD Eanble HM01 HM04 HM05 HM06
4 | SUPPLY_ALK | Supply alkali to cip skid | 0 | 0 | 0 | 0 | 0 | A1 | 1 | 1 | 0 | A2 | A2 | 0 | 0 | 0 | 0 | 0 | A3 | SP2 | 0 | 1 | A4 | MSG0: Alkali is supplying. MSG1:PT-ALK01 - xx barg. A1:Open VLV_DELAY_TM, then close A2:If supply to DS1/DS2 cip skid, open PV-ALK10.If supply to DS3/DS4 cip skid, open PV-ALK11. A3:Set SP2=PU_SUP_SPD. Delay PU_DELAY_TM, then start A4:Set agitator speed = AG_SPD Eanble HM01 HM03 HM04 HM05 HM06
5 | ADD_ALK | Add alkali to alkali tank | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | sp=0 | 0 | 0 | sp=0 | MSG0: Adding alkali. MSG1: Wait for operator confirmed Eanble HM01 HM04 HM05 HM06
5 | ADD_PW | Add pw to alkali tank | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | sp=0 | 1 | 0 | sp=0 | MSG0: Adding pw MSG1:Wait tank level LIT-310301>=ALK_LE_SP A1:Send REQ_PW= 1. Eanble HM01 HM02 HM04 HM05 HM06
6 | DRAIN | Alkali tank drain
7 | CIP | Alkali tank CIP
Notes:
a) | DRAIN see SFC DRAIN and RUN table DRAIN
b) | CIP see SFC CIP and RUN table CIP

## RUN Table DRAIN
Step |  | Description | TAG1 | TAG2 | TAG3 | TAG4 | TAG5 | TAG6 | TAG7 | TAG8 | TAG9 | TAG10 | TAG11 | TAG12 | TAG13 | TAG14 | TAG15 | TAG16 | TAG17 |  | TAG18 | TAG19 |  | Actions
|  |  | PV-ALK01 | PV-ALK02 | PV-ALK03 | PV-ALK04 | PV-ALK05 | PV-ALK06 | PV-ALK07 | PV-ALK08 | PV-ALK09 | PV-ALK10 | PV-ALK11 | PV-ALK26 | PV-ALK39 | PV-ALK40 | PV-ALK41 | PV-ALK45 | PU-ALK02 | SIC-01 | PV-ALK50 | AG-ALK01
S0100 | LEVEL_CHK | 液位检查 check tank level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | sp=0 | 0 | 0 | sp=0 | MSG0: Check tank level.
T0200 | LIT-310301 >= AT_LE_L
S0200 | AIRBLOW_DRAIN | 吹扫排放 Drain tank by airblow | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | sp=0 | 0 | 0 | sp=0 | MSG0: Airblow drain MSG1: Wait tank level LIT-310301<AT_LE_L
T0300 | LIT-310301<AT_LE_L
T0300-1 | LIT-310301<AT_LE_L
S0300 | DRAIN_GRAVITY | 罐子重力自排 Drain tank by gravity | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | sp=0 | 0 | 0 | sp=0 | MSG0: Gravity drain MSG1: Wait DRN_ELAP_TM elasped
T0400 | DRN_ELAP_TM elasped
S0400 | SET_STATE | 设置状态 Set state | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | sp=0 | 0 | 0 | sp=0 | MSG0: Change TK state A1: Change tank state to Empty
Note:
a)

## RUN Table CIP
Step |  | Description | TAG1 | TAG2 | TAG3 | TAG4 | TAG5 | TAG6 | TAG7 | TAG8 | TAG9 | TAG10 | TAG11 | TAG12 | TAG13 | TAG14 | TAG15 | TAG16 | TAG17 |  | TAG18 | TAG19 |  | Actions
|  |  | PV-ALK01 | PV-ALK02 | PV-ALK03 | PV-ALK04 | PV-ALK05 | PV-ALK06 | PV-ALK07 | PV-ALK08 | PV-ALK09 | PV-ALK10 | PV-ALK11 | PV-ALK26 | PV-ALK39 | PV-ALK40 | PV-ALK41 | PV-ALK45 | PU-ALK02 | SIC-01 | PV-ALK50 | AG-ALK01
T0100 | CYC_WASH_TM elapsed
S0100 | LEVEL_CHK | 液位检查 check tank level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | sp=0 | 0 | 0 | sp=0 | MSG0: Check tank level.
T0200 | LIT-310301 >= AT_LE_L
S0200 | AIRBLOW_DRAIN | 吹扫排放 Drain tank by airblow | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | sp=0 | 0 | 0 | sp=0 | MSG0: Airblow drain MSG1: Wait tank level LIT-310301<AT_LE_L
T0300 | LIT-310301<AT_LE_L
T0300-1 | LIT-310301<AT_LE_L
S0300 | DRAIN_GRAVITY | 罐子重力自排 Drain tank by gravity | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | sp=0 | 0 | 0 | sp=0 | MSG0: Gravity drain MSG1: Wait DRN_ELAP_TM elasped
T0400 | DRN_ELAP_TM elapsed and AT_WASH_TIMES<AT_TIMES_SP
S0400 | SELF_WASH | 罐子自清洗 Tank selfwash and drain | 1 | A3 | A3 | A3 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | A3 | 0 | 0 | sp=0 | A1 | 1 | sp=0 | MSG0: Tank self wash and drain MSG1: Wait SELF_WASH_TM elasped A1: Send REQ_PW = 1.When PW is ready, start timer SELF_WASH_TM A2(SELF_WASH_TM complete): Send REQ_PW = 0. A3: cycle pulse open VLV_PULSE_TM.
T0500 | SELF_WASH_TM elapsed
S0500 | PUMP_CYCLE | 自循环清洗 Tank selfwash with pump cycle | 1 | 1 | 1 | 1 | 0 | A4 | 1 | 1 | 0 | A4 | A4 | 1 | 1 | 0 | 0 | 0 | A3 | SP1 | A1 | 1 | sp=0 | MSG0: Tank selfwash with pump cycle MSG1: Wait CYC_WASH_TM elasped A1: Enable REQ_PW Force SP (AT_LT_CYC<LIT-310301<WT_LE_M),If LIT-310301 <=AT_LT_CYC then REQ_PW=1,else if LIT-310301 >=WT_LE_M,then REQ_PW=0 A2: Until tank level LIT-310301>AT_LT_CYC, start timer CYC_WASH_TM A3(after A2): SP1=PU_CIR_SPD, Delay PU_DELAY_TM, Then Start Pump. A4: cycle pulse open VLV_PULSE_TM. A5: WT_WASH_TIMES +1 A6: After CYC_WASH_TM elapsed, stop PU-ALK02
T0600 | DRN_ELAP_TM elapsed and AT_WASH_TIMES>=AT_TIMES_SP
S0600 | SET_STATE | 设置状态 Set state | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | sp=0 | 0 | 0 | sp=0 | MSG0: Change TK state A1: Change tank state to Clean
Note:
a)

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max | REV.2a
| PU_CIR_SPD | No | Pump Speed for recirculation | real | Hz | 25 | 15 | 50
| PU_SUP_SPD | Phase | Pump Speed for supply alkali to CIP skid | real | Hz | 25 | 15 | 50
| AG_SPD | No | Agitator Speed for mix | real | Hz | 25 | 15 | 50
| PU_DELAY_TM | No | Pump delay time to start | int | s | 20 | 1 | 60
| VLV_DELAY_TM | No | Valve delay close time | int | s | 20 | 1 | 60
| AT_LE_LL | No | Alkali tank low low level | real | L | 100 | 1 | 2500
| AT_LE_L | No | Alkali tank low level | real | L | 200 | 1 | 2500
| AT_LE_M | No | Alkali tank middle level | real | L | 600 | 1 | 2500
| AT_LT_CYC | No | Alkali tank cycle level | real | L | 400 | 1 | 2500
| PRES_L_SP | No | low Pressure SP while pump running | real | barg | 1 | 0 | 5
| AT_TIMES_SP | No | Alkali tank wash Times setpoint | int | NA | 1 | 1 | 10
| DRN_ELAP_TM | No | Drain elapse time | real | min | 2 | 1 | 10
| SELF_WASH_TM | No | Self Wash elapse time | real | min | 2 | 1 | 10
| CYC_WASH_TM | No | Pump cycle wash elapse time | real | min | 2 | 1 | 10
| CU_FB_TM | No | Max time for CU feed back | real | min | 1 | 1 | 10
| ALK_LE_SP | Phase | Alkali level setpoint | real | L | 1000 | 1 | 1200
备注
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description | Eng.Unit | Step | Begin | End
X
X
12 | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| HM01 |  | Emergency Stop E-ALK01
| HM02 |  | CU_FB_TM elasped
| HM03 |  | PT-ALK01<PRES_L_SP when pump run for 15s
| HM04 |  | LIT-310301:Alkali Tank level fault
| HM05 |  | PT-ALK01:Supply pressure fault
| HM06 |  | PIT-ALK01:Alkali tank pressure fault