## Cover Sheet
Phase Specification
PH_TC_TK
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. Winatech |  | Revision
M2b Project |  |  | PP20-0098-T-004230 |  | 2.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-04-12 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-04-12 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-31 | 王树深
| 0.1a | 2020-11-20 | 王树深 | hold/abort 更新
| 0.1b | 2020-12-10 | 王树深 | 1.参数ΔT1改为TT_SP1_DEV，ΔT2改为TT_SP1_DEV。 2.Action Table中个别commend改正及EM_PUR_PS的补充。
| 1.0 | 2021-03-03 | 王树深 | 程序仿真修改
| 2.0 | 2021-04-12 | 王树深 | 增加急停编号

## Description
6. | Description
The Phase PH_TC_TK is used for heating jacket by TCU water or cooling jacket by glycol water. 1. This phase includes 3 cases: JC_HEAT,JC_COOL, DEACTIVE 2. JC_HEAT is used for heating product by TCU water through jacket. 3. JC_COOL is used for cooling product by chilled water or glycol water through jacket. 4. DEACTIVE is used for ending temperature control in process tank.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| Harvest System | DSX-TA02
| Purification System | DSX-TA03
DSX-TA04
DSX-TA05
DSX-TA06
DSX-TA08
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit Class | Equiment Module
| Harvest System | EM_PUR_JC
EM_TCU
EM_PUR_PS
| Purification System | EM_PUR_JC
EM_TCU
EM_PUR_PS
EM's at other Units (Shared EM's)
| Unit Class | Equiment Module
| N/A | N/A
Notes:
a) | "X" in Units and Equipment Module represents Line number. "X" can be 1, 2, 3, 4.

## SFC_RUN_2 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_3 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_4 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_5 (hidden)
8 | RUN Logic without Check Steps

## SFC_CHECK
8. | SFC Check Steps for RUN Logic

## SFC_RUN
8. | RUN Logic with Check Steps
|  | Phase name | TT(Note1):
|  | DSXTA02_JACKET | TIT-DSXTA0201
|  | DSXTA03_JACKET | TIT-DSXTA0301
|  | DSXTA04_JACKET | TIT-DSXTA0401
|  | DSXTA05_JACKET | TIT-DSXTA0501
|  | DSXTA06_JACKET | TIT-DSXTA0601
|  | DSXTA08_JACKET | TIT-DSXTA0801
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic
Phase name
DSXTA02_JACKET
DSXTA03_JACKET
DSXTA04_JACKET
DSXTA05_JACKET
DSXTA06_JACKET
DSXTA08_JACKET
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
Unit Class |  | Phase |  | EM
Harvest system |  | DSXTA02_JACKET | EM_DSXTA02_JC | EM_DSXPUR_PS | EM_DSXTCU01
Purification System |  | DSXTA03_JACKET | EM_DSXTA03_JC | EM_DSXPUR_PS | EM_DSXTCU01
|  | DSXTA04_JACKET | EM_DSXTA04_JC | EM_DSXPUR_PS | EM_DSXTCU01
|  | DSXTA05_JACKET | EM_DSXTA05_JC | EM_DSXPUR_PS | EM_DSXTCU01
|  | DSXTA06_JACKET | EM_DSXTA06_JC | EM_DSXPUR_PS | EM_DSXTCU01
|  | DSXTA08_JACKET | EM_DSXTA08_JC | EM_DSXPUR_PS | EM_DSXTCU01
Step |  | Description | EM_PUR_JC | EM_PUR_PS | EM_TCU | Alarm Settings | Controller Settings | Other Actions | REV.2
S9000 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 Check if all the EM are free or not | N/A | N/A | N/A
S9010 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A
S9020 | STATE_CHECK | 状态检查，检查STATE是否正确 Check if the STATE is correct or not | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A
S9040 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A
S9060 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A | N/A
S1000 | GLW_FILL | 夹套通入温控水 Heat filled with TCM water | JC_GLW_HEAT | N/A | GLW_FILL | Enable "Step time alarm" if GLW_FILL_TM_SP when Step_Timer is over
S1010 | GLW_CIRC | 夹套通入温控水开泵循环 Heat filled with TCM water circulate by pump | JC_GLW_HEAT | N/A | GLW_FILL_PU
S1020 | JC_HEAT | 夹套通入温控水进行加热 Heat jacket by TCM | JC_GLW_HEAT | PS_SUPPLY | GLW_CIR_TC |  | R_TT_SP1 - R_TT_SP1_DEV≤TT(Note1)≤R_TT_SP1 + R_TT_SP1_DEV
S2000 | JC_COOL | 夹套通入冷冻水或者冷媒进行冷却 Cool jacket by CHW or GLW | JC_COOL | CLOSE | CLOSE |  | TT(Note1)≤R_TT_SP2 + R_TT_SP2_DEV1 | Release EM:EM_PUR_PS
S2010 | TEMP_CONL | 夹套通入冷冻水或者冷媒进行温度控制 Temperture control jacket by CHW or GLW | JC_COOL_PUL | N/A | CLOSE |  | R_TT_SP2 - R_TT_SP2_DEV2≤TT(Note1)≤R_TT_SP2 + R_TT_SP2_DEV2
S3000 | DEACTIVE | 停止夹套控制 Stop tank jacket control | JC_BW_BK | CLOSE | GLW_DRN | Enable "Step time alarm" if R_DR_TM when Step_Timer is over |  | Release EM:EM_PUR_PS
S3010 | JC_BLOW | 夹套内介质排尽后吹扫 Blow jacket | JC_BW_BK | N/A | GLW_DRN | Enable "Step time alarm" if R_JC_BLOW when Step_Timer is over
S3020 | CLOSE | 关闭所有阀门。 Close all valve. | CLOSE | N/A | CLOSE
S7010 | HOLD | 暂停 pause | HOLD | HOLD | HOLD
S8010 | ABORT | 中止 Abort | CLOSE | CLOSE | CLOSE |  |  | Release EM:EM_PUR_PS
S8020 | SET STATE | 设置状态。 Set State. | CLOSE | CLOSE | CLOSE |  |  | Set State as 'READY'
Notes:
a) | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max | REV.2a
| CS_SEL 1: JACKET_HEAT | YES | Heating jacket by glycol water from TCU, it isn't self-finished. | Name Set | N/A | 1 | 0 | 100
| CS_SEL 2: JACKET_COOL | YES | Cooling jacket by cold glycol water from utility, it isn't self-finished. | Name Set | N/A | 2 | 0 | 100
| CS_SEL 3: DEACTIVE | YES | Stop tank temperature control. | Name Set | N/A | 3 | 0 | 100
| R_GLW_FILL_TM | NO | Timer for glycol water filling into jacket | int | min | 5 | 0 | 30
| R_TT_SP1 | YES | Tank temperature set point | int | °C | 22 | 0 | 100
| R_TT_SP1_DEV | YES | Deviation | int | °C | 2 | 0 | 100
| R_TT_SP2 | YES | Tank temperature set point | int | °C | 6 | 0 | 20
| R_TT_SP2_DEV1 | YES | Deviation | int | °C | 1 | 0 | 20
| R_TT_SP2_DEV2 | YES | Deviation | int | °C | 0.5 | 0 | 20
| R_DR_TM | NO | Jacket drain timer | int | min | 2 | 1 | 30
| R_BLOW_TM | YES | Jacket blow timer | int | min | 5 | 0 | 30
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description | Type | Eng.Unit | Step | Begin | End
12 | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXPUR01/E-DSXPUR02/E-DSXPUR03/E-DSXPUR04/E-DSXPUR05/E-DSXPUR06 Emergency Stop
| Hold03 |  | TT fault
13 | Indication Table
| Code |  | Description
| prompt |  | Step timer S130~170 elapsed

## ALARM (hidden)
INDICATION | S150~S180