## Cover Sheet
Phase Specification
PH_LT_PUR_DS1_3
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-004237 |  | 2.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-04-12 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-04-12 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-31 | 王树深 | Draft for review
| 0.1a | 2020-11-20 | 王树深 | hold/abort 更新
| 0.1b | 2020-12-10 | 王树深 | phase更新
| 1.0 | 2021-03-18 | 王树深 | 程序仿真修改
| 2.0 | 2021-04-12 | 王树深 | 增加急停编号

## Description
6. | Description
The Phase is used for tank hermetic test.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| Process Tank(DPS) | DSXTA02
DSXTA03
DSXTA04
DSXTA05
DSXTA06
DSXTA08
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit Class | Equiment Module
| Media Prep Tank | EM_MP_CIPR_PU
EM_MP_TKP_CIPS
EM_MP_TKP_CIPR
| Harvest system-1 | EM_HV1_CIPR_PU
EM_HV1_TKP_CIPS
EM_HV1_TKP_CIPR
EM_FA0113
EM_FA0115
| Media Prep Tank Harvest system-1 | EM_TXXXX_HEADER
EM_TXXXX_TOP
EM_TXXXX_BOM
EM_FAXXXX
| buffer Prep Tank | EM_TK_TOP
EM_TK_HEADER
EM_TK_BOM
EM_TK_FA
EM_BP_TKP_CIPS
EM_BP_TKP_CIPR
EM_CIPR_PU
| buffer Hold Tank | EM_TK_TOP
EM_TK_HEADER
EM_TK_BOM
EM_TK_FA
EM_BH_TKP_CIPS
EM_BH_TKP_CIPR
EM_CIPR_PU
EM's at other Units (Shared EM's)
| Unit Class | Equiment Module
| Process Tank(DPS) | EM_PUR_TOP
EM_PUR_BOM
EM_PUR_FA1
EM_PUR_FA2
EM_PUR_PD_OUT
EM_CHT_PD_IN
EM_DF03
EM_DF03_FILT
EM_DF04
EM_VF01_IN_DIS
EM_VF01_FILT
EM_PUR_PD_IN
Notes:
a) | "X" in Units and Equipment Module represents Line number. "X" can be 1, 2, 3, 4.

## SFC_RUN_2 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_3 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_4 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_5 (hidden)
8 | RUN Logic without Check Steps

## SFC_CHECK
8. | RUN Logic with Check Steps

## SFC_RUN
8. | RUN Logic with Check Steps
|  | Phase | Note1
|  | LT_DSXTA02 | PIT-DSXTA0201
|  | LT_DSXTA03 | PIT-DSXTA0301
|  | LT_DSXTA04 | PIT-DSXTA0401
|  | LT_DSXTA05 | PIT-DSXTA0501
|  | LT_DSXTA06 | PIT-DSXTA0601
|  | LT_DSXTA08 | PIT-DSXTA0801

## SFC_HOLD_ABORT
8. HOLD and ABORT Logic

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
Unit Class |  | Phase(Note3) | EM
Purification System |  | LT_DSXTA02_CHT01 | EM_DSXTA02_TOP | EM_DSXTA02_BOM | N/A | EM_DSXTA02_FA | N/A | EM_DSXCHT01_PDIN | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | LT_DSXTA03_DF03 | EM_DSXTA03_TOP | EM_DSXTA03_BOM | EM_DSXTA03_FA | N/A | N/A | N/A | EM_DSXDF03 | EM_FDSXDF0301 | N/A | N/A | N/A | N/A | N/A
|  | LT_DSXTA04_CHT02 | EM_DSXTA04_TOP | EM_DSXTA04_BOM | EM_DSXTA04_FA | N/A | N/A | EM_DSXCHT02_PDIN | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | LT_DSXTA05_CHT03 | EM_DSXTA05_TOP | EM_DSXTA05_BOM | EM_DSXTA05_FA | N/A | EM_DSXTA05_PDOUT | EM_DSXCHT03_PDIN | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | LT_DSYTA05_UF01 | EM_DSXTA05_TOP | EM_DSXTA05_BOM | EM_DSXTA05_FA | N/A | EM_DSXTA05_PDOUT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | LT_DSYTA06_UF01 | EM_DSXTA06_TOP | EM_DSXTA06_BOM | EM_DSXTA06_FA | N/A | EM_DSXTA06_PDOUT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | LT_DSXTA05_VF01 | EM_DSXTA05_TOP | EM_DSXTA05_BOM | EM_DSXTA05_FA | N/A | EM_DSXTA05_PDOUT | N/A | N/A | N/A | EM_DSXDF04 | EM_DSXVF01IN_DIS | EM_FDSXVF0101 | N/A | N/A
|  | LT_DSXTA06_VF01 | EM_DSXTA06_TOP | EM_DSXTA06_BOM | EM_DSXTA06_FA | N/A | N/A | N/A | N/A | N/A | EM_DSXDF04 | EM_DSXVF01IN_DIS | EM_FDSXVF0101 | N/A | N/A
|  | LT_DSYTA08_UF02 | EM_DSXTA08_TOP | EM_DSXTA08_BOM | EM_DSXTA08_FA | N/A | EM_DSXTA08_PDOUT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | LT_DSXTA08_TA06 | EM_DSXTA08_TOP | EM_DSXTA08_BOM | EM_DSXTA08_FA | N/A | EM_DSXTA08_PDOUT | N/A | N/A | N/A | N/A | N/A | N/A | EM_DSXTA06_PD_IN | EM_DSXTA06_TOP
Step |  | Description | EM_PUR_TOP | EM_PUR_BOM | EM_PUR_FA1 | EM_PUR_FA2 | EM_PUR_PD_OUT | EM_CHT_PD_IN | EM_DF03 | EM_DF03_FILT | EM_DF04 | EM_VF01_IN_DIS | EM_VF01_FILT | EM_PUR_PD_IN | EM_PUR_TOP | Alarm Settings | Controller Settings | Other Actions
S9000 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 Check if all the EM are free or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9010 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9020 | STATE_CHECK | 状态检查，检查STATE是否正确 Check if the STATE is correct or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9040 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9060 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S1010 | PA_SUP | 通过压空进行罐体建压。 Tank set pressure by PA. | CLOSE | AT | PRESSURE_CONT | PRESSURE_CONT | Note1 | PD_IN_PR | PD_IN | PD_TS2 | Note2 | PD_TO_PU | PE_PR | PD2_TO_TK | PD_IN_AT
S1020 | STABLE | 稳定时间 Stable time | CLOSE | AT | AT_TK | AT_TK | Note1 | PD_IN_PR | PD_IN | PD_TS2 | Note2 | PD_TO_PU | PE_PR | PD2_TO_TK | PD_IN_AT
S1030 | PT_CHECK | 记录罐内初始压力。 Record initial pressure of tank. | CLOSE | AT | AT_TK | AT_TK | Note1 | PD_IN_PR | PD_IN | PD_TS2 | Note2 | PD_TO_PU | PE_PR | PD2_TO_TK | PD_IN_AT
S1040 | PT_CHECK | 记录罐内终点压力。 Record final pressure of tank. | CLOSE | AT | AT_TK | AT_TK | Note1 | PD_IN_PR | PD_IN | PD_TS2 | Note2 | PD_TO_PU | PE_PR | PD2_TO_TK | PD_IN_AT
S1050 | ALARM | 压降超过设定值，报警 Alarm if pressure drop exceeds set point. | CLOSE | AT | AT_TK | AT_TK | Note1 | PD_IN_PR | PD_IN | PD_TS2 | Note2 | PD_TO_PU | PE_PR | PD2_TO_TK | PD_IN_AT
S1060 | RELIEF | 压力泄放 Pressure relief | CLOSE | AT | VENT_FA | VENT_FA | Note1 | PD_IN_PR | PD_IN | PD_TS2 | Note2 | PD_TO_PU | PE_PR | PD2_TO_TK | PD_IN_AT
S1070 | CLOSE | 关闭阀门 Close valves | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE
S7000 | HOLD | 暂停 Hold | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD
S8100 | ABORT | 中止步骤 Abort | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE
S8200 | SET STATE | 设置状态 Set state | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE |  |  | set state to dirty
|  |  |  | Phase | Note1 | Note2
|  |  |  | LT_DSXTA05_CHT03 | PD_OUT3 | N/A
|  |  |  | LT_DSYTA05_UF01 | PD_OUT2 | N/A
|  |  |  | LT_DSYTA06_UF01 | PD_OUT2 | N/A
|  |  |  | LT_DSYTA08_UF02 | PD_OUT1 | N/A
|  |  |  | LT_DSXTA08_TA06 | PD_OUT2 | N/A
|  |  |  | LT_DSXTA05_NF01 | PD_OUT1 | PD_FR_TA05
|  |  |  | LT_DSXTA06_NF01 | PD_OUT1 | PD_FR_TA06
Note3："X" in "DSX" represents Line number. "X" can be 1,2,3,4。"Y" in "DSY" represents Line number. "Y" can be 1, 3。"Z" in "DSZ" represents Line number. "Z" can be 2, 4

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| R_TA05_LT_SEL | YES | TA05_CHT03 | N/A | N/A | N/A | N/A | N/A
|  |  | TA05_DSYUF01 | N/A | N/A | N/A | N/A | N/A
|  |  | TA05_VF01 | N/A | N/A | N/A | N/A | N/A
| R_TA06_LT_SEL | YES | TA06_DSYUF01 | N/A | N/A | N/A | N/A | N/A
|  |  | TA06_VF01 | N/A | N/A | N/A | N/A | N/A
| R_TA08_LT_SEL | YES | TA08_DSYUF02 | N/A | N/A | N/A | N/A | N/A
|  |  | TA08_TA06 | N/A | N/A | N/A | N/A | N/A
| R_PT_SP | Yes | Tank set pressure. | real | barg | 1 | 0.1 | 2
| R_STABLE_TM | Yes | Time for PT stable | int | min | 2 | 0 | 30
| R_HOLD_TM | Yes | Time for hermetic test | int | min | 10 | 1 | 100
| R_DP_SP | Yes | Tank pressure drop acceptale point. | real | barg/min | 0.05 | 0 | 2
| R_RELIEF_TM | Yes | Time for Pressure relief | int | sec | 10 | 0 | 600
| R_PT_SP_DEV | Yes | Deviation of tank pressure setting. | real | barg | 0.1 | 0 | 1
| R_PT_SP2 | Yes | Set pressure. | real | barg | 0.5 | 0.1 | 2
| R_PT_RELEASE | YES | Set Point for Releasing Tank Pressure. | real | barg | 0.2 | 0 | 2
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description | Type | Eng.Unit | Step | Begin | End
| L_HOLD_TM_PV | Yes | Time for hermetic test | int
| L_dP_PV | Yes | Tank pressure drop acceptale | int
12. | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSYPUR01/E-DSYPUR02/E-DSYPUR03/E-DSYPUR04/E-DSYPUR05/E-DSYPUR06 Emergency Stop
| Hold03 |  | PT(Note1) fault
| Hold04 |  | PT1- PT(Note1) > R_PT_SP2

## ALARM (hidden)
INDICATION | S150~S180