## Cover Sheet
Phase Specification
PH_VAL_CWFI_PUR
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-004257 |  | 2.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-04-12 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-04-12 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-30 | 杜林茂 | Draft
| 0.1a | 2020-12-06 | 杜林茂 | 1. SFC_RUN：删除S1060, S1070 2. SFC_HOLD_ABORT: 删除S7000，S8000 3. Action Table: 删除EM_PUR_CIPR，EM_PUR_CIPR_PU，EM_BCIP_CIPR，EM_C_RTN对应内容； 删除S1050，S1060，S7000，S8000对应内容； EM_PUR_HEAD中Command改为CIP_IN； EM_PUR_TOP中Command改为CIP_IN； EM_PUR_FA1，EM_PUR_FA2对应command改为VENT_FA； EM_PUR_BOM对应Command改为TK_DRN； 删除Note4，5，7； 完善Note 10内容 4. ParameterHold Tables：删除R_Level_Empty，增加R_TM_CWFI_DRN
| 2.0 | 2021-04-12 | 王树深 | 增加急停编号

## Description
6. | Description
The Phase VAL_CWFI_PUR is used for validation of CWFI into tank. 1. DCS will control the POU valve which supplied and installed by CU system.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class |  | Units
| Process Tank (DPS) |  | 4000L HARVEST TANK UNIT TA02
4000L PURIFICATION TANK UNIT TA03
4000L PURIFICATION TANK UNIT TA04
4000L PURIFICATION TANK UNIT TA05
3000L PURIFICATION TANK UNIT TA06
3000L PURIFICATION TANK UNIT TA08
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit Class | Equiment Module
| Process Tank (DPS) | EM_PUR_HEAD
EM_PUR_TOP
EM_PUR_FA1
EM_PUR_BOM
EM_PUR_CIPS1
EM_PUR_FA2
EM's at other Units (Shared EM's)
| Unit Class | Equiment Module
| CIP Station | EM_C_CIP
EM_C_SUP
EM_C_BTH
| Buffer Preparation Tank | EM_BCIP_CIPS

## SFC_RUN_2 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_3 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_4 (hidden)
8 | RUN Logic without Check Steps

## SFC_RUN_5 (hidden)
8 | RUN Logic without Check Steps

## SFC_CHECK
8. | RUN Logic with Check Steps
| Note2: | R_SELECT_STATION is 03 or 05. Default of R_SELECT_STATION can be modified.
If R_SELECT_STATION is 03, select CIP03 if CIP03 is standby. Select CIP05 if CIP03 is occupied.

## SFC_RUN
8. | RUN Logic with Check Steps
|  | Phase (Note2) | Note1
|  | VAL_CWFI_DXSTA02 | WIT-DSXTA0201
|  | VAL_CWFI_DXSTA03 | WIT-DSXTA0301
|  | VAL_CWFI_DXSTA04 | WIT-DSXTA0401
|  | VAL_CWFI_DXSTA05 | WIT-DSXTA0501
|  | VAL_CWFI_DXSTA06 | WIT-DSXTA0601
|  | VAL_CWFI_DXSTA08 | WIT-DSXTA0801
Note3: | "X" in "DSX" represents Line number. "X" can be 1, 2, 3, 4.

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic
Note1: Continue with last step in RUN when RESTART.
Note2: R_MAX_TM_STEP in RUN shall be reset when RESTART.

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
| Unit Class | Phase
| Purification System | VAL_CWFI_DSXTA02 | EM_DSXCIP02 | EM_DSXCIP02_SUP | EM_DSXCIP02_BTH | N/A | EM_DSXPUR_CIPS1 | EM_DSXTA02_HEAD | EM_DSXTA02_TOP | N/A | EM_DSXTA02_FA1 | EM_DSXTA02_BOM
|  | VAL_CWFI_DSXTA03 | [5 empty] | EM_DSXTA03_HEAD | EM_DSXTA03_TOP | EM_DSXTA03_FA | N/A | EM_DSXTA03_BOM
|  | VAL_CWFI_DSXTA04 | [5 empty] | EM_DSXTA04_HEAD | EM_DSXTA04_TOP | EM_DSXTA04_FA | N/A | EM_DSXTA04_BOM
|  | VAL_CWFI_DSXTA05 | [5 empty] | EM_DSXTA05_HEAD | EM_DSXTA05_TOP | EM_DSXTA05_FA | N/A | EM_DSXTA05_BOM
|  | VAL_CWFI_DSXTA06 | [5 empty] | EM_DSXTA06_HEAD | EM_DSXTA06_TOP | EM_DSXTA06_FA | N/A | EM_DSXTA06_BOM
|  | VAL_CWFI_DSXTA08 | EM_DSXCIP03/EM_DSXCIP05 (Note1) | EM_DSXCIP03_SUP/EM_DSXCIP05_SUP (Note2) | EM_DSXCIP03_BTH/EM_DSXCIP05_BTH (Note4) | EM_DSXCIP03_CIPS/EM_DSXCIP05_CIPS (Note3) | N/A | EM_DSXTA08_HEAD | EM_DSXTA08_TOP | EM_DSXTA08_FA | N/A | EM_DSXTA08_BOM
Step |  | Description | EM_C_CIP | EM_C_SUP | EM_C_BTH | EM_BCIP_CIPS | EM_PUR_CIPS1 | EM_PUR_HEAD | EM_PUR_TOP | EM_PUR_FA1 | EM_PUR_FA2 | EM_PUR_BOM | Alarm Settings | Controller Settings | Other Actions
S9000 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 Check if all the EM are free or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9010 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9020 | STATE_CHECK | 状态检查，检查STATE是否正确 Check if the STATE is correct or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9040 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S9060 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S1010 | CHECK_MEDIUM | 检查介质 Check medium | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
S1020 | PREP_MEDIUM | 准备介质 CIP station medium preparation | PREP_CWFI | STOP | WT_FILTER_OPEN | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | Enable "H&M" if execution of step time exceeds R_MAX_TM_STEP2
S1030 | FILLING | 注水 Fill the tank with CWFI | SUPPLY_CWFI | MEDIUM_SUPPLY | WT_FILTER_OPEN | CIP_TO_TA08 | Note6 | CIP_IN | CIP_IN | VENT_FA | VENT_FA | CLOSE
S1040 | CWFI_SAMPLE | CWFI取样 CWFI sample | STOP_PUMP | MEDIUM_SUPPLY | WT_FILTER_OPEN | CIP_TO_TA08 | Note6 | CIP_IN | CIP_IN | VENT_FA | VENT_FA | CLOSE |  |  | Operator sample CWFI in tank
S1050 | DRAIN | 罐内水排放 Drain the tank | STOP | STOP | STOP | CLOSE | CLOSE | CLOSE | CLOSE | VENT_FA | VENT_FA | TK_DRN
S1080 | CLOSE | 关闭所有设备 Close all device | STOP | STOP | STOP | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE
S7010 | HOLD | 暂停 Hold | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD
S8010 | ABORT | 中止步骤 Abort | STOP | STOP | STOP | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE
Note1: If select CIP03 station, EM will be EM_DSXCIP03. If select CIP05 station, EM will be EM_DSXCIP05. | [5 empty] | Unit Class | Phase | Note6
Note2: If select CIP03 station, EM will be EM_DSXCIP03_SUP. If select CIP05 station, EM will be EM_DSXCIP05_SUP. | [5 empty] | Purification System | VAL_CWFI_DXSTA02 | N/A
Note3: If select CIP03 station, EM will be EM_DSXCIP03_CIPS. If select CIP05 station, EM will be EM_DSXCIP05_CIPS. | [6 empty] | VAL_CWFI_DXSTA03 | CIP_TO_TA03
Note4: If select CIP03 station, EM will be EM_DSXCIP03_BTH. If select CIP05 station, EM will be EM_DSXCIP05_BTH. | [6 empty] | VAL_CWFI_DXSTA04 | CIP_TO_TA04
[7 empty] | VAL_CWFI_DXSTA05 | CIP_TO_TA05
[7 empty] | VAL_CWFI_DXSTA06 | CIP_TO_TA06
[7 empty] | VAL_CWFI_DXSTA08 | N/A

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| R_PUR_WT_SP | YES | Weight setpoint of PUR tank CWFI filling | real | kg | 1000 | 0 | 10000
| R_MAX_TM_STEP | NO | Maximum step execution time, hold if exceed the time | real | min | 30 | 0 | 120
| R_TM_CWFI_DRN | YES | Drain time for CWFI in tank and pipe | real | min | 10 | 1 | 30
| R_SELECT_STATION | NO | Preferred CIP Station selected | N/A | N/A | CIP03 or CIP05 | N/A | N/A
| R_WT_DR_SP | YES | Weight setpoint of PUR tank Drain | real | kg | 10 | 0 | 1000
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description |  | Eng. Unit | Step | Begin | End
| N/A |  | N/A |  | N/A | N/A | N/A | N/A
12. | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXPUR01/E-DSXPUR02/E-DSXPUR03/E-DSXPUR04/E-DSXPUR05/E-DSXPUR06 Emergency Stop
| Hold03 |  | WIT fault
| Hold04 |  | R_MAX_TM_STEP elapsed
| Hold05 |  | CIP station Hold

## ALARM (hidden)
INDICATION | S150~S180