## Cover Sheet
Phase Specification
PH_ALM
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-010235 |  | 2.0
| Initials | Date |  | Signature
Morimatsu prepared: | 王树深 | 2021-04-12 |  | 王树深
Morimatsu approved: | 张蓉蓉 | 2021-04-12 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-12-10 | 吴婷
| 1.0 | 2021-03-03 | 王树深 | SFAT修改
| 2.0 | 2021-04-12 | 王树深 | 增加急停编号

## Description
6. | Description
The Phase PH_ALM is used for monitoring the PH or CT or temperature of tank.When the PH or CT or temperature exceeds a certain value, alarm .
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| Process Tank(DPS) | TA02
| Process Tank(DPS) | TA03
| Process Tank(DPS) | TA04
| Process Tank(DPS) | TA05
| Process Tank(DPS) | TA06
| Process Tank(DPS) | TA08
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit Class | Equiment Module
| N/A | N/A
EM's at other Units (Shared EM's)
| Unit Class | Equiment Module
| N/A | N/A

## SFC_RUN
8. | RUN Logic with Check Steps

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
Unit Class |  | Phase
Process Tank(DPS) |  | PH_ALM_TA02 | N/A | AIT-DS1TA0202 | TIT-DS1TA0201
Process Tank(DPS) |  | PH_ALM_TA03 | AIT-DS1TA0301 | AIT-DS1TA0302 | TIT-DS1TA0301
Process Tank(DPS) |  | PH_ALM_TA04 | AIT-DS1TA0401 | AIT-DS1TA0402 | TIT-DS1TA0401
Process Tank(DPS) |  | PH_ALM_TA05 | AIT-DS1TA0501 | AIT-DS1TA0502 | TIT-DS1TA0501
Process Tank(DPS) |  | PH_ALM_TA06 | AIT-DS1TA0601 | AIT-DS1TA0602 | TIT-DS1TA0601
Process Tank(DPS) |  | PH_ALM_TA08 | AIT-DS1TA0801 | AIT-DS1TA0802 | TIT-DS1TA0801
Step |  | Description | AIT01 | AIT02 | TIT01 | Report Record | Alarm Settings | Controller Settings | Other Actions
S1010 | CHECK | 检查 check | A1 | A1 | A1 | record AIT01 or AIT02 or TIT01 alarm or not | A1
S7000 | HOLD | 暂停 pause
S8000 | ABORT | 结束。 End.
A1:Set R_PH_ALM_EN,R_PH_H_ALM,R_PH_L_ALM to AIT02 module
Set R_CT_ALM_EN,R_CT_H_ALM,R_CT_L_ALM to AIT01 module
Set R_TEMP_ALM_EN,R_TEMP_H_ALM,R_TEMP_L_ALM to TIT01 module
If Thisunit = "TA02",AIT02 is AIT-DS1TA0202,TIT01 is TT-DS1TA0201
If Thisunit = "TA03",AIT01 is AIT-DS1TA0301,AIT02 is AIT-DS1TA0302,TIT01 is TT-DS1TA0301
If Thisunit = "TA04",AIT01 is AIT-DS1TA0401,AIT02 is AIT-DS1TA0402,TIT01 is TT-DS1TA0401
If Thisunit = "TA05",AIT01 is AIT-DS1TA0501,AIT02 is AIT-DS1TA0502,TIT01 is TT-DS1TA0501
If Thisunit = "TA06",AIT01 is AIT-DS1TA0601,AIT02 is AIT-DS1TA0602,TIT01 is TT-DS1TA0601
If Thisunit = "TA08",AIT01 is AIT-DS1TA0801,AIT02 is AIT-DS1TA0802,TIT01 is TT-DS1TA0801

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| R_PH_ALM_EN | YES | Enable PH check | Boolean | Enable Disable | PENDING | PENDING | PENDING
| R_PH_H_ALM | YES | High PH for alarm | real | M/A | PENDING | PENDING | PENDING
| R_PH_L_ALM | YES | Low PH for alarm | real | M/A | PENDING | PENDING | PENDING
| R_PH_HH_ALM | YES | High-high PH for alarm | real | M/A | PENDING | PENDING | PENDING
| R_PH_LL_ALM | YES | Low-low PH for alarm | real | M/A | PENDING | PENDING | PENDING
| R_CT_ALM_EN | YES | Enable CT check | Boolean | Enable Disable | PENDING | PENDING | PENDING
| R_CT_H_ALM | YES | High CT for alarm | real | M/A | PENDING | PENDING | PENDING
| R_CT_L_ALM | YES | Low CT for alarm | real | M/A | PENDING | PENDING | PENDING
| R_CT_HH_ALM | YES | High-high CT for alarm | real | M/A | PENDING | PENDING | PENDING
| R_CT_LL_ALM | YES | Low-low CT for alarm | real | M/A | PENDING | PENDING | PENDING
| R_TEMP_ALM_EN | YES | Enable TEMP check | Boolean | Enable Disable | PENDING | PENDING | PENDING
| R_TEMP_H_ALM | YES | High TEMP for alarm | real | M/A | PENDING | PENDING | PENDING
| R_TEMP_L_ALM | YES | Low TEMP for alarm | real | M/A | PENDING | PENDING | PENDING
| R_TEMP_HH_ALM | YES | High-high TEMP for alarm | real | M/A | PENDING | PENDING | PENDING
| R_TEMP_LL_ALM | YES | Low-low TEMP for alarm | real | M/A | PENDING | PENDING | PENDING
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description | Type | Eng.Unit | Step | Begin | End
12. | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXPUR01/E-DSXPUR02/E-DSXPUR03/E-DSXPUR04/E-DSXPUR05/E-DSXPUR06 Emergency Stop