## Cover Sheet
Phase Specification
PH_BUF_VD_TM
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-011064 |  | 1.0
| Initials | Date |  | Signature
Morimatsu prepared: | 吴婷 | 2021-04-26 |  | 吴婷
Morimatsu approved: | 杜林茂 | 2021-04-26 |  | 杜林茂
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 1 | 2021-04-26 | 吴婷

## Description
6. | Description
The Phase PH_BUF_VD_TM is for input validity parameters of buffer state.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| BP Tank | 3000L BUFFER PREPARATION TANK UNIT TA12
3000L BUFFER PREPARATION TANK UNIT TA13
6000L BUFFER PREPARATION TANK UNIT TA14
9000L BUFFER PREPARATION TANK UNIT TA15
| BH Tank | 3000L BUFFER HOLDING TANK UNIT TA16
3000L BUFFER HOLDING TANK UNIT TA17
3000L BUFFER HOLDING TANK UNIT TA18
3000L BUFFER HOLDING TANK UNIT TA19
3000L PROCESS WATER TANK UNIT TA20
3000L BUFFER HOLDING TANK UNIT TA21
3000L BUFFER HOLDING TANK UNIT TA22
3000L BUFFER HOLDING TANK UNIT TA23
3000L BUFFER HOLDING TANK UNIT TA24
6000L BUFFER HOLDING TANK UNIT TA26
6000L BUFFER HOLDING TANK UNIT TA27
6000L BUFFER HOLDING TANK UNIT TA28
6000L BUFFER HOLDING TANK UNIT TA29
3000L BUFFER HOLDING TANK UNIT TA30
6000L BUFFER HOLDING TANK UNIT TA31
9000L 0.5M NaOH TANK UNIT TA32
9000L BUFFER HOLDING TANK UNIT TA33
9000L BUFFER HOLDING TANK UNIT TA34
9000L BUFFER HOLDING TANK UNIT TA35
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit Class | Equiment Module
| N/A | N/A
EM's at other Units (Shared EM's)
| Unit Class | Equiment Module
| N/A | N/A

## SFC_RUN
8. | RUN Logic with Check Steps

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
Unit Class |  | STATE
BP Tank |  | DSX_TA12_TK
DSX_TA13_TK
DSX_TA14_TK
DSX_TA15_TK
BH Tank |  | DSX_TA16_TK
DSX_TA17_TK
DSX_TA18_TK
DSX_TA19_TK
DSX_TA20_TK
DSX_TA21_TK
DSX_TA22_TK
DSX_TA23_TK
DSX_TA24_TK
DSX_TA26_TK
DSX_TA27_TK
DSX_TA28_TK
DSX_TA29_TK
DSX_TA30_TK
DSX_TA31_TK
DSX_TA32_TK
DSX_TA33_TK
DSX_TA34_TK
DSX_TA35_TK
BP Tank |  | DSX_TA12_X_TP03
DSX_TA13_X_TP03
DSX_TA14_X_TP02
DSX_TA15_X_TP01
DSX_TP01_X_TP02
DSX_TP02_X_TP03
DSX_TP01_X_TA32
DSX_TP01_X_TA33
DSX_TP01_X_TA34
DSX_TP01_X_TA35
DSX_TP02_X_TA26
DSX_TP02_X_TA27
DSX_TP02_X_TA28
DSX_TP02_X_TA29
DSX_TP02_X_TA31
DSX_TP03_X_TA18
DSX_TP03_X_TA22
DSX_TP03_X_TA24
DSX_TP03_X_TA17
DSX_TP03_X_TA19
DSX_TP03_X_TA21
DSX_TP03_X_TA23
DSX_TP03_X_TA30
DSX_TP03_X_SUBAG
Step |  | Description | Report Record | Alarm Settings | Controller Settings | Other Actions
S1010 | SET_VD_TM | 设置效期时间 Set valid time |  |  |  | set valid time to R_P_XXX/R_D_XXX/R_C_XXX/R_S_XXX
S7010 | HOLD | 暂停 pause
S8010 | ABORT | 中止 Abort
Note1: Process Warning when time ≥ R_P_XXX minus R_P_WARN Dirty Warning when time ≥ R_D_XXX minus R_D_WARN Clean Warning when time ≥ R_C_XXX minus R_C_WARN SIPed Warning when time ≥ R_S_XXX minus R_S_WARN
Note2:X in DSX represents Line number. "X" can be 1, 2, 3, 4.

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| R_P_TA12_TK | Yes | TA12 process Valid time | int | h | 24 | 0 | 9999 | 1
| R_P_TA13_TK | Yes | TA13 process Valid time | int | h | 24 | 0 | 9999 | 2
| R_P_TA14_TK | Yes | TA14 process Valid time | int | h | 24 | 0 | 9999 | 3
| R_P_TA15_TK | Yes | TA15 process Valid time | int | h | 24 | 0 | 9999 | 4
| R_P_TA16_TK | Yes | TA16 process Valid time | int | h | 24 | 0 | 9999 | 5
| R_P_TA17_TK | Yes | TA17 process Valid time | int | h | 24 | 0 | 9999 | 6
| R_P_TA18_TK | Yes | TA18 process Valid time | int | h | 24 | 0 | 9999 | 7
| R_P_TA19_TK | Yes | TA19 process Valid time | int | h | 24 | 0 | 9999 | 8
| R_P_TA20_TK | Yes | TA20 process Valid time | int | h | 24 | 0 | 9999 | 9
| R_P_TA21_TK | Yes | TA21 process Valid time | int | h | 24 | 0 | 9999 | 10
| R_P_TA22_TK | Yes | TA22 process Valid time | int | h | 24 | 0 | 9999 | 11
| R_P_TA23_TK | Yes | TA23 process Valid time | int | h | 24 | 0 | 9999 | 12
| R_P_TA24_TK | Yes | TA24 process Valid time | int | h | 24 | 0 | 9999 | 13
| R_P_TA26_TK | Yes | TA26 process Valid time | int | h | 24 | 0 | 9999 | 14
| R_P_TA27_TK | Yes | TA27 process Valid time | int | h | 24 | 0 | 9999 | 15
| R_P_TA28_TK | Yes | TA28 process Valid time | int | h | 24 | 0 | 9999 | 16
| R_P_TA29_TK | Yes | TA29 process Valid time | int | h | 24 | 0 | 9999 | 17
| R_P_TA30_TK | Yes | TA30 process Valid time | int | h | 24 | 0 | 9999 | 18
| R_P_TA31_TK | Yes | TA31 process Valid time | int | h | 24 | 0 | 9999 | 19
| R_P_TA32_TK | Yes | TA32 process Valid time | int | h | 24 | 0 | 9999 | 20
| R_P_TA33_TK | Yes | TA33 process Valid time | int | h | 24 | 0 | 9999 | 21
| R_P_TA34_TK | Yes | TA34 process Valid time | int | h | 24 | 0 | 9999 | 22
| R_P_TA35_TK | Yes | TA35 process Valid time | int | h | 24 | 0 | 9999 | 23
| R_DHT | Yes | Dirty Valid time | int | h | 48 | 0 | 9999 | 24
| R_D_TA12_TK | Yes | TA12 Dirty Valid time | int | h | 48 | 0 | 9999 | 25
| R_D_TA13_TK | Yes | TA13 Dirty Valid time | int | h | 48 | 0 | 9999 | 26
| R_D_TA14_TK | Yes | TA14 Dirty Valid time | int | h | 48 | 0 | 9999 | 27
| R_D_TA15_TK | Yes | TA15 Dirty Valid time | int | h | 48 | 0 | 9999 | 28
| R_D_TA16_TK | Yes | TA16 Dirty Valid time | int | h | 48 | 0 | 9999 | 29
| R_D_TA17_TK | Yes | TA17 Dirty Valid time | int | h | 48 | 0 | 9999 | 30
| R_D_TA18_TK | Yes | TA18 Dirty Valid time | int | h | 48 | 0 | 9999 | 31
| R_D_TA19_TK | Yes | TA19 Dirty Valid time | int | h | 48 | 0 | 9999 | 32
| R_D_TA20_TK | Yes | TA20 Dirty Valid time | int | h | 48 | 0 | 9999 | 33
| R_D_TA21_TK | Yes | TA21 Dirty Valid time | int | h | 48 | 0 | 9999 | 34
| R_D_TA22_TK | Yes | TA22 Dirty Valid time | int | h | 48 | 0 | 9999 | 35
| R_D_TA23_TK | Yes | TA23 Dirty Valid time | int | h | 48 | 0 | 9999 | 36
| R_D_TA24_TK | Yes | TA24 Dirty Valid time | int | h | 48 | 0 | 9999 | 37
| R_D_TA26_TK | Yes | TA26 Dirty Valid time | int | h | 48 | 0 | 9999 | 38
| R_D_TA27_TK | Yes | TA27 Dirty Valid time | int | h | 48 | 0 | 9999 | 39
| R_D_TA28_TK | Yes | TA28 Dirty Valid time | int | h | 48 | 0 | 9999 | 40
| R_D_TA29_TK | Yes | TA29 Dirty Valid time | int | h | 48 | 0 | 9999 | 41
| R_D_TA30_TK | Yes | TA30 Dirty Valid time | int | h | 48 | 0 | 9999 | 42
| R_D_TA31_TK | Yes | TA31 Dirty Valid time | int | h | 48 | 0 | 9999 | 43
| R_D_TA32_TK | Yes | TA32 Dirty Valid time | int | h | 48 | 0 | 9999 | 44
| R_D_TA33_TK | Yes | TA33 Dirty Valid time | int | h | 48 | 0 | 9999 | 45
| R_D_TA34_TK | Yes | TA34 Dirty Valid time | int | h | 48 | 0 | 9999 | 46
| R_D_TA35_TK | Yes | TA35 Dirty Valid time | int | h | 48 | 0 | 9999 | 47
| R_D_TA12_X_TP03 | Yes | TA12 X TP03 Dirty Valid time | int | h | 48 | 0 | 9999 | 48
| R_D_TA13_X_TP03 | Yes | TA13 X TP03 Dirty Valid time | int | h | 48 | 0 | 9999 | 49
| R_D_TA14_X_TP02 | Yes | TA14 X TP02 Dirty Valid time | int | h | 48 | 0 | 9999 | 50
| R_D_TA15_X_TP01 | Yes | TA15 X TP01 Dirty Valid time | int | h | 48 | 0 | 9999 | 51
| R_D_TP01_X_TP02 | Yes | TP01 X TP02 Dirty Valid time | int | h | 48 | 0 | 9999 | 52
| R_D_TP02_X_TP03 | Yes | TP02 X TP03 Dirty Valid time | int | h | 48 | 0 | 9999 | 53
| R_D_TP02_X_TA31 | Yes | TP02 X TA31 Dirty Valid time | int | h | 48 | 0 | 9999 | 54
| R_D_TP03_X_TA18 | Yes | TP03 X TA18 Dirty Valid time | int | h | 48 | 0 | 9999 | 55
| R_D_TP03_X_SUBAG | Yes | TP03 X SUBAG Dirty Valid time | int | h | 48 | 0 | 9999 | 56
| R_CHT | Yes | Clean Valid time | int | h | 72 | 0 | 9999 | 57
| R_C_TA12_TK | Yes | TA12 Clean Valid time | int | h | 72 | 0 | 9999 | 58
| R_C_TA14_TK | Yes | TA14 Clean Valid time | int | h | 72 | 0 | 9999 | 59
| R_C_TA15_TK | Yes | TA15 Clean Valid time | int | h | 72 | 0 | 9999 | 60
| R_C_TA20_TK | Yes | TA20 Clean Valid time | int | h | 72 | 0 | 9999 | 61
| R_C_TA31_TK | Yes | TA31 Clean Valid time | int | h | 72 | 0 | 9999 | 62
| R_C_TA35_TK | Yes | TA35 Clean Valid time | int | h | 72 | 0 | 9999 | 63
| R_C_TA12_X_TP03 | Yes | TA12 X TP03 Clean Valid time | int | h | 72 | 0 | 9999 | 64
| R_C_TA13_X_TP03 | Yes | TA13 X TP03 Clean Valid time | int | h | 72 | 0 | 9999 | 65
| R_C_TA14_X_TP02 | Yes | TA14 X TP02 Clean Valid time | int | h | 72 | 0 | 9999 | 66
| R_C_TA15_X_TP01 | Yes | TA15 X TP01 Clean Valid time | int | h | 72 | 0 | 9999 | 67
| R_C_TP01_X_TP02 | Yes | TP01 X TP02 Clean Valid time | int | h | 72 | 0 | 9999 | 68
| R_C_TP02_X_TP03 | Yes | TP02 X TP03 Clean Valid time | int | h | 72 | 0 | 9999 | 69
| R_C_TP02_X_TA28 | Yes | TP02 X TA28 Clean Valid time | int | h | 72 | 0 | 9999 | 70
| R_SHT | Yes | SIPed Valid time | int | h | 72 | 0 | 9999 | 71
| R_S_TA12_TK | Yes | TA12 SIPed Valid time | int | h | 72 | 0 | 9999 | 72
| R_S_TA14_TK | Yes | TA14 SIPed Valid time | int | h | 72 | 0 | 9999 | 73
| R_S_TA15_TK | Yes | TA15 SIPed Valid time | int | h | 72 | 0 | 9999 | 74
| R_S_TA20_TK | Yes | TA20 SIPed Valid time | int | h | 72 | 0 | 9999 | 75
| R_S_TA31_TK | Yes | TA31 SIPed Valid time | int | h | 72 | 0 | 9999 | 76
| R_S_TA35_TK | Yes | TA35 SIPed Valid time | int | h | 72 | 0 | 9999 | 77
| R_S_TA12_X_TP03 | Yes | TA12 X TP03 SIPed Valid time | int | h | 72 | 0 | 9999 | 78
| R_S_TA13_X_TP03 | Yes | TA13 X TP03 SIPed Valid time | int | h | 72 | 0 | 9999 | 79
| R_S_TA14_X_TP02 | Yes | TA14 X TP02 SIPed Valid time | int | h | 72 | 0 | 9999 | 80
| R_S_TA15_X_TP01 | Yes | TA15 X TP01 SIPed Valid time | int | h | 72 | 0 | 9999 | 81
| R_S_TP01_X_TP02 | Yes | TP01 X TP02 SIPed Valid time | int | h | 72 | 0 | 9999 | 82
| R_S_TP02_X_TP03 | Yes | TP02 X TP03 SIPed Valid time | int | h | 72 | 0 | 9999 | 83
| R_S_TP02_X_TA28 | Yes | TP02 X TA28 SIPed Valid time | int | h | 72 | 0 | 9999 | 84
| R_P_WARN | Yes | Warning time before process date | int | h | 8 | 0 | 9999
| R_D_WARN | Yes | Warning time before for dirty date | int | h | 8 | 0 | 9999
| R_C_WARN | Yes | Warning before time for clean date | int | h | 12 | 0 | 9999
| R_S_WARN | Yes | Warning time before for SIPed date | int | h | 12 | 0 | 9999
| R_X | Yes | Line number 1 | nameset | N/A | 1
|  | Yes | Line number 2 | nameset | N/A | 2
|  | Yes | Line number 3 | nameset | N/A | 3
|  | Yes | Line number 4 | nameset | N/A | 4
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description | Type | Eng.Unit | Step | Begin | End
12. | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXPUR01/E-DSXPUR02/E-DSXPUR03/E-DSXPUR04/E-DSXPUR05/E-DSXPUR06/E-DSXBH01/E-DSXBP01/E-DSXCIP02/E-DSXCIP03/E-DSXCIP05 Stop