## Cover Sheet
Phase Specification
PH_PUR_VD_TM
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-011065 |  | 1.0
| Initials | Date |  | Signature
Morimatsu prepared: | 吴婷 | 2021-04-26 |  | 吴婷
Morimatsu approved: | 杜林茂 | 2021-04-26 |  | 杜林茂
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 1 | 2021-04-26 | 吴婷

## Description
6. | Description
The Phase PH_PUR_VD_TM is for input validity parameters of purification state.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| BH Tank | 3000L BUFFER HOLDING TANK UNIT TA16
3000L BUFFER HOLDING TANK UNIT TA17
3000L BUFFER HOLDING TANK UNIT TA18
3000L BUFFER HOLDING TANK UNIT TA19
3000L PROCESS WATER TANK UNIT TA20
3000L BUFFER HOLDING TANK UNIT TA21
3000L BUFFER HOLDING TANK UNIT TA22
3000L BUFFER HOLDING TANK UNIT TA23
3000L BUFFER HOLDING TANK UNIT TA24
6000L BUFFER HOLDING TANK UNIT TA26
6000L BUFFER HOLDING TANK UNIT TA27
6000L BUFFER HOLDING TANK UNIT TA28
6000L BUFFER HOLDING TANK UNIT TA29
3000L BUFFER HOLDING TANK UNIT TA30
6000L BUFFER HOLDING TANK UNIT TA31
9000L 0.5M NaOH TANK UNIT TA32
9000L BUFFER HOLDING TANK UNIT TA33
9000L BUFFER HOLDING TANK UNIT TA34
9000L BUFFER HOLDING TANK UNIT TA35
| Process Tank(DPS) | 4000L HARVEST TANK UNIT TA02
4000L PURIFICATION TANK UNIT TA03
4000L PURIFICATION TANK UNIT TA04
4000L PURIFICATION TANK UNIT TA05
3000L PURIFICATION TANK UNIT TA06
3000L PURIFICATION TANK UNIT TA08
| Process Equipment 无需信号交互 | DEPTH FILTRATION UNIT DF03
NF WORK UNIT NF01
| Process Equipment 都是DCS系统，内部交互 | HPLC #1 WORK UNIT CHT01
HPLC #2 WORK UNIT CHT02
HPLC #3 WORK UNIT CHT03
| 超滤 都是DCS系统，内部交互 | UF/DF WORK UNIT UF01 for Line 1 and Line 3
UF/DF WORK UNIT UF02 for Line 1 and Line 3
UF/DF WORK UNIT UF01 for Line 2 and Line 4
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit Class | Equiment Module
| N/A | N/A
EM's at other Units (Shared EM's)
| Unit Class | Equiment Module
| N/A | N/A

## SFC_RUN
8. | RUN Logic with Check Steps

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
Unit Class |  | STATE
BH Tank |  | DSX_TA16_X_DIS
DSX_TA16_X_TA01
Process Equipment 都是DCS系统，内部交互 |  | DSX_TA16_X_CHT01
DSX_TA17_X_CHT01
DSX_TA18_X_CHT01
DSX_TA19_X_CHT01
BH Tank |  | DSX_TA21_X_DIS
Process Equipment 无需信号交互 |  | DSX_TA21_X_DF03
Process Tank(DPS) |  | DSX_TA21_X_TA03
BH Tank |  | DSX_TA22_X_DIS
Process Equipment 都是DCS系统，内部交互 |  | DSX_TA22_X_CHT03
DSX_TA22_X_CHT02
DSX_TA23_X_CHT03
BH Tank |  | DSX_TA24_X_DIS
超滤 都是DCS系统，内部交互 |  | DSY_TA24_X_UF01
Process Equipment 都是DCS系统，内部交互 |  | DSX_TA24_X_CHT03
DSX_TA27_X_CHT01
DSX_TA28_X_CHT02
BH Tank |  | DSX_TA29_X_DIS
Process Tank(DPS) |  | DSX_TA29_X_TA04
Process Equipment 都是DCS系统，内部交互 |  | DSX_TA29_X_CHT02
BH Tank |  | DSX_TA30_X_DIS
Process Equipment 无需信号交互 |  | DSX_TA30_X_VF01
Process Tank(DPS) |  | DSX_TA30_X_TA06
超滤 都是DCS系统，内部交互 |  | DSY_TA30_X_UF02
DSY_TA31_X_UF02
BH Tank |  | DSX_TA33_X_DIS
DSX_TA33_X_TA01
Process Equipment 都是DCS系统，内部交互 |  | DSX_TA33_X_CHT01
BH Tank |  | DSX_TA34_X_DIS
Process Equipment 无需信号交互 |  | DSX_TA34_X_DF03
Process Equipment 都是DCS系统，内部交互 |  | DSX_TA34_X_CHT01
DSX_TA34_X_CHT02
BH Tank |  | DSX_TA35_X_DIS
Process Tank(DPS) |  | DSX_TA35_X_TA05
Process Equipment 都是DCS系统，内部交互 |  | DSX_TA35_X_CHT03
BH Tank |  | DSX_TA20_X_DIS
Process Equipment 都是DCS系统，内部交互 |  | DSX_TA20_X_CHT01
DSX_TA20_X_CHT02
DSX_TA20_X_CHT03
超滤 都是DCS系统，内部交互 |  | DSY_TA20_X_UF01
DSY_TA20_X_UF02
Process Equipment 无需信号交互 |  | DSX_TA20_X_NF01
Process Tank(DPS) |  | DSX_TA20_X_TA03
DSX_TA20_X_TA04
Process Equipment 无需信号交互 |  | DSX_TA20_X_DF03
BH Tank |  | DSX_TA26_X_DIS
Process Equipment 都是DCS系统，内部交互 |  | DSX_TA26_X_CHT01
DSX_TA26_X_CHT02
DSX_TA26_X_CHT03
超滤 都是DCS系统，内部交互 |  | DSY_TA26_X_UF01
DSY_TA26_X_UF02
BH Tank |  | DSX_TA32_X_DIS
Process Equipment 都是DCS系统，内部交互 |  | DSX_TA32_X_CHT01
DSX_TA32_X_CHT02
DSX_TA32_X_CHT03
超滤 都是DCS系统，内部交互 |  | DSY_TA32_X_UF01
DSY_TA32_X_UF02
Process Tank(DPS) |  | DSX_TA02_TK
DSX_TA03_TK
DSX_TA04_TK
DSX_TA05_TK
DSX_TA06_TK
DSX_TA08_TK
DSX_TA01_X_TA02
Process Equipment 都是DCS系统，内部交互 |  | DSX_TA02_X_CHT01
DSX_CHT01_X_TA03
Process Equipment 无需信号交互 |  | DSX_TA03_X_DF03
DSX_DF03_X_TA04
Process Equipment 都是DCS系统，内部交互 |  | DSX_TA04_X_CHT02
DSX_CHT02_X_TA05
DSX_TA05_X_CHT03
DSX_CHT03_X_TA06
Process Equipment 无需信号交互 |  | DSX_TA05_X_VF01
DSX_TA06_X_VF01
DSX_VF01_X_TA08
超滤 都是DCS系统，内部交互 |  | DSY_TA05_X_UF01
DSY_TA06_X_UF01
Process Tank(DPS) |  | DSX_TA08_X_TA06
超滤 都是DCS系统，内部交互 |  | DSY_TA08_X_UF02
超滤 都是DCS系统，内部交互 |  | DSZ_TA30_X_UF01 |  |  |  |  | 新增
|  | DSZ_TA31_X_UF01 |  |  |  |  | 新增
|  | DSZ_TA20_X_UF01 |  |  |  |  | 新增
|  | DSZ_TA26_X_UF01 |  |  |  |  | 新增
|  | DSZ_TA32_X_UF01 |  |  |  |  | 新增
|  | DSZ_TA08_X_UF01 |  |  |  |  | 新增
Step |  | Description | Report Record | Alarm Settings | Controller Settings | Other Actions
S1010 | SET_VD_TM | 设置效期时间 Set valid time |  |  |  | set valid time to R_P_XXX/R_D_XXX/R_C_XXX/R_S_XXX
S7010 | HOLD | 暂停 pause
S8010 | ABORT | 中止 Abort
Note1: Process Warning when time ≥ R_P_XXX-R_P_WARN Dirty Warning when time ≥ R_D_XXX-R_D_WARN Clean Warning when time ≥ R_C_XXX-R_C_WARN SIPed Warning when time ≥ R_S_XXX-R_S_WARN
Note2:X in DSX represents Line number. "X" can be 1, 2, 3, 4.
"Y" in "DSY" represents Line number. "Y" can be 1, 3。"Z" in "DSZ" represents Line number. "Z" can be 2, 4

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| R_P_TA02_TK | Yes | TA02 process Valid time | int | h | 24 | 0 | 9999 | 1
| R_P_TA03_TK | Yes | TA03 process Valid time | int | h | 24 | 0 | 9999 | 2
| R_P_TA04_TK | Yes | TA04 process Valid time | int | h | 24 | 0 | 9999 | 3
| R_P_TA05_TK | Yes | TA05 process Valid time | int | h | 24 | 0 | 9999 | 4
| R_P_TA06_TK | Yes | TA06 process Valid time | int | h | 24 | 0 | 9999 | 5
| R_P_TA08_TK | Yes | TA08 process Valid time | int | h | 24 | 0 | 9999 | 6
| R_DHT | Yes | Dirty Valid time | int | h | 48 | 0 | 9999 | 7
| R_D_TA18_X_CHT01 | Yes | TA18_X_CHT01 Dirty Valid time | int | h | 48 | 0 | 9999 | 8
| R_D_TA31_X_UF02 | Yes | TA18_X_CHT01 Dirty Valid time | int | h | 48 | 0 | 9999 | 9
| R_D_TA02_TK | Yes | TA02 Dirty Valid time | int | h | 48 | 0 | 9999 | 10
| R_D_TA03_TK | Yes | TA03 Dirty Valid time | int | h | 48 | 0 | 9999 | 11
| R_D_TA04_TK | Yes | TA04 Dirty Valid time | int | h | 48 | 0 | 9999 | 12
| R_D_TA05_TK | Yes | TA05 Dirty Valid time | int | h | 48 | 0 | 9999 | 13
| R_D_TA06_TK | Yes | TA06 Dirty Valid time | int | h | 48 | 0 | 9999 | 14
| R_D_TA08_TK | Yes | TA08 Dirty Valid time | int | h | 48 | 0 | 9999 | 15
| R_D_TA01_X_TA02 | Yes | TA01 X TA02 Dirty Valid time | int | h | 48 | 0 | 9999 | 16
| R_D_TA02_X_CHT01 | Yes | TA02 X CHT01 Dirty Valid time | int | h | 48 | 0 | 9999 | 17
| R_D_CHT01_X_TA03 | Yes | CHT01 X TA03 Dirty Valid time | int | h | 48 | 0 | 9999 | 18
| R_D_TA03_X_DF03 | Yes | TA03 X DF03 Dirty Valid time | int | h | 48 | 0 | 9999 | 19
| R_D_DF03_X_TA04 | Yes | DF03 X TA04 Dirty Valid time | int | h | 48 | 0 | 9999 | 20
| R_D_TA04_X_CHT02 | Yes | TA04 X CHT02 Dirty Valid time | int | h | 48 | 0 | 9999 | 21
| R_D_CHT02_X_TA05 | Yes | CHT02 X TA05 Dirty Valid time | int | h | 48 | 0 | 9999 | 22
| R_D_TA05_X_CHT03 | Yes | TA05 X CHT03 Dirty Valid time | int | h | 48 | 0 | 9999 | 23
| R_D_CHT03_X_TA06 | Yes | CHT03 X TA06 Dirty Valid time | int | h | 48 | 0 | 9999 | 24
| R_D_TA05_X_VF01 | Yes | TA05 X VF01 Dirty Valid time | int | h | 48 | 0 | 9999 | 25
| R_D_TA06_X_VF01 | Yes | TA06 X VF01 Dirty Valid time | int | h | 48 | 0 | 9999 | 26
| R_D_VF01_X_TA08 | Yes | VF01 X TA08 Dirty Valid time | int | h | 48 | 0 | 9999 | 27
| R_D_TA05_X_UF01 | Yes | TA05 X UF01 Dirty Valid time | int | h | 48 | 0 | 9999 | 28
| R_D_TA06_X_UF02 | Yes | TA06 X UF02 Dirty Valid time | int | h | 48 | 0 | 9999 | 29
| R_D_TA08_X_TA06 | Yes | TA08 X TA06 Dirty Valid time | int | h | 48 | 0 | 9999 | 30
| R_D_TA08_X_UF02 | Yes | TA08 X UF02 Dirty Valid time | int | h | 48 | 0 | 9999 | 31
| R_CHT | Yes | Clean Valid time | int | h | 72 | 0 | 9999 | 32
| R_C_TA21_X_DF03 | Yes | TA21 X DF03 Clean Valid time | int | h | 72 | 0 | 9999 | 33
| R_C_TA31_X_UF02 | Yes | C TA31 X UF02 Clean Valid time | int | h | 72 | 0 | 9999 | 34
| R_C_TA02_TK | Yes | TA02 Clean Valid time | int | h | 72 | 0 | 9999 | 35
| R_C_TA03_TK | Yes | TA03 Clean Valid time | int | h | 72 | 0 | 9999 | 36
| R_C_TA06_TK | Yes | TA06 Clean Valid time | int | h | 72 | 0 | 9999 | 37
| R_C_CHT03_X_TA06 | Yes | CHT03 X TA06 Clean Valid time | int | h | 72 | 0 | 9999 | 38
| R_C_TA05_X_VF01 | Yes | TA05 X VF01 Clean Valid time | int | h | 72 | 0 | 9999 | 39
| R_SHT | Yes | SIPed Valid time | int | h | 72 | 0 | 9999 | 40
| R_S_TA21_X_DF03 | Yes | TA21 X DF03 SIPed Valid time | int | h | 72 | 0 | 9999 | 41
| R_S_TA31_X_UF02 | Yes | C TA31 X UF02 SIPed Valid time | int | h | 72 | 0 | 9999 | 42
| R_S_TA02_TK | Yes | TA02 SIPed Valid time | int | h | 72 | 0 | 9999 | 43
| R_S_TA03_TK | Yes | TA03 SIPed Valid time | int | h | 72 | 0 | 9999 | 44
| R_S_TA06_TK | Yes | TA06 SIPed Valid time | int | h | 72 | 0 | 9999 | 45
| R_S_CHT03_X_TA06 | Yes | CHT03 X TA06 SIPed Valid time | int | h | 72 | 0 | 9999 | 46
| R_S_TA05_X_VF01 | Yes | TA05 X VF01 SIPed Valid time | int | h | 72 | 0 | 9999 | 47
| R_D_TA31_X_UF01 | Yes | TA31_X_UF01 Dirty Valid time | int | h | 48 | 0 | 9999 | 新增
| R_C_TA31_X_UF01 | Yes | TA31_X_UF01 Clean Valid time | int | h | 72 | 0 | 9999 | 新增
| R_S_TA31_X_UF01 | Yes | TA31_X_UF01 SIPed Valid time | int | h | 72 | 0 | 9999 | 新增
| R_D_TA08_X_UF01 | Yes | TA08_X_UF01 Dirty Valid time | int | h | 48 | 0 | 9999 | 新增
| R_P_WARN | Yes | Warning time before process date | int | h | 8 | 0 | 9999
| R_D_WARN | Yes | Warning time before for dirty date | int | h | 8 | 0 | 9999
| R_C_WARN | Yes | Warning before time for clean date | int | h | 12 | 0 | 9999
| R_S_WARN | Yes | Warning time before for SIPed date | int | h | 12 | 0 | 9999
| R_X | Yes | Line number 1 | nameset | N/A | 1
|  | Yes | Line number 2 | nameset | N/A | 2
|  | Yes | Line number 3 | nameset | N/A | 3
|  | Yes | Line number 4 | nameset | N/A | 4
| R_Y | Yes | Line number 1 | nameset | N/A | 1
|  | Yes | Line number 3 | nameset | N/A | 3
| R_Z | Yes | Line number 2 | nameset | N/A | 2
|  | Yes | Line number 4 | nameset | N/A | 4
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description | Type | Eng.Unit | Step | Begin | End
12. | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXPUR01/E-DSXPUR02/E-DSXPUR03/E-DSXPUR04/E-DSXPUR05/E-DSXPUR06/E-DSXBH01/E-DSXBP01/E-DSXCIP02/E-DSXCIP03/E-DSXCIP05 Stop