## Cover Sheet
Phase Specification PH_X_PUR_CHT
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-004199 |  | 2.0
| Initials | Date |  | Signature
Morimatsu prepared: | 吴婷 | 2021-04-26 |  | 吴婷
Morimatsu approved: | 张蓉蓉 | 2021-04-26 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-10-30 | 吴婷 | Draft for review
| 0.1a | 2020-11-18 | 吴婷 | 1.ACTION TABILE 增加一个CM； 2.ACTION TABILE中EM_PUR_FA1/EM_PUR_FA2拆开
| 0.1b | 2020-11-20 | 吴婷 | ACTION TABLE 删除CM,HOLD,ABORT顺控图修改
| 0.1c | 2020-12-10 | 吴婷 | HOLD Table新增
| 1.0 | 2021-03-03 | 吴婷 | 根据程序仿真修改
| 2.0 | 2021-04-26 | 吴婷 | 增加急停编号，删除效期参数。

## Description
6. | Description
The Phase is used for transferring product from process tank to chromatography.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| Process Equipment 都是DCS系统，内部交互 | HPLC #1 WORK UNIT CHT01
HPLC #2 WORK UNIT CHT02
HPLC #3 WORK UNIT CHT03
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at own Unit
| Unit | Equiment Module
| Process Equipment 都是DCS系统，内部交互 | EM_CHT_PD_IN
EM's at other Units (Shared EM's)
| Unit | Equiment Module
| Process Tank(DPS) | EM_PUR_BOM | EM_PUR_FA1 | EM_PUR_FA2 | EM_PUR_PD_OUT

## SFC_CHECK
8. | SFC Check Steps for RUN Logic

## SFC_RUN
8. | RUN Logic without Check Steps
BF反向排气，另写PHASE，用平衡液排气，每个层析使用前都要排
|  | Phase | Note 1
|  | Phase: X_PUR_CHT01 CS_SEL_1: TA02_TO_CHT01 | WT_DSXTAxx01=WT_DSXTA0201
|  | Phase:X_PUR_CHT02 CS_SEL_1: TA04_TO_CHT02 | WT_DSXTAxx01=WT_DSXTA0401
|  | Phase: X_PUR_CHT03 CS_SEL_1: TA05_TO_CHT03 | WT_DSXTAxx01=WT_DSXTA0501
报警后，层析关闭，反馈信号给罐子，罐子才关阀

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
|  | Phase | EM
|  | Phase: X_PUR_CHT01 CS_SEL_1: TA02_TO_CHT01 | EM_DSXTA02_BOM | N/A | EM_DSXTA02_FA1 | N/A | EM_DSXCHT01_PDIN | EM_DSXTA02_FA2
|  | Phase:X_PUR_CHT02 CS_SEL_1: TA04_TO_CHT02 | EM_DSXTA04_BOM | EM_DSXTA04_FA | N/A | N/A | EM_DSXCHT02_PDIN | N/A
|  | Phase: X_PUR_CHT03 CS_SEL_1: TA05_TO_CHT03 | EM_DSXTA05_BOM | EM_DSXTA05_FA | N/A | EM_DSXTA05_PDOUT | EM_DSXCHT03_PDIN | N/A
Step |  | Description | EM_PUR_BOM | EM_PUR_FA1 | EM_PUR_FA2 | EM_PUR_PD_OUT | EM_CHT_PD_IN | EM_PUR_FA3 | Report Record | Alarm Settings | Controller Settings | Other Actions
S9000 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 Check if all the EM are free or not | N/A | N/A | N/A | N/A | N/A | N/A
S9010 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A
S9020 | STATE_CHECK | 状态检查，检查STATE是否正确 Check if the STATE is correct or not | N/A | N/A | N/A | N/A | N/A | N/A
S9030 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A
S9040 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A | N/A | N/A | N/A | N/A
S9050 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A | N/A | N/A | N/A | N/A
S9060 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A | N/A | N/A | N/A | N/A
S1010 | MSG | 提示层析和软管是否准备就绪？ Prompt CHTxx ready and hose connected. | N/A | N/A | N/A | N/A | N/A | N/A
S1020 | PD_SUP | 物料转移到用点 Product supply to point of use | PD_OUT | PRESSURE_CONT | PRESSURE_CONT | Note2 | PD_IN | PA_TK | Record WT_DSXTAxx01 Note 3 |  | EM_PUR_FA1/EM_PUR_FA2：SP=R_PT_SP1 △P=R_△P1
S1030 | ALARM | 上样罐低液位报警 Loading tank low level alarm. | PD_OUT | PRESSURE_CONT | PRESSURE_CONT | Note2 | PD_IN | PA_TK
S1040 | DELAY | 等待层析反馈信号 Wait until CHT to feedback message. | PD_OUT | PRESSURE_CONT | PRESSURE_CONT | Note2 | PD_IN | PA_TK
S1050 | CLOSE | 关闭所有阀门。 Close all valve. | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | Record WT_DSXTAxx01 Note 3
S1060 | SET_STATE | 重置状态 set state | CLOSE | VENT_FA | VENT_FA | CLOSE | CLOSE | CLOSE |  |  |  | Source Tank=Dirty Line State = Dirty
S7010 | HOLD | 暂停 pause | HOLD | HOLD | HOLD | HOLD | HOLD | HOLD
S8010 | ABORT | 关闭所有阀门。 Close all valve. | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE | CLOSE
S8020 | SET_STATE | 重置状态 set state | CLOSE | VENT_FA | VENT_FA | CLOSE | CLOSE | CLOSE |  |  |  | Source Tank:Process Line State = Process
|  | Phase | Note2 | Note 3
|  | Phase: X_PUR_CHT01 CS_SEL_1: TA02_TO_CHT01 | N/A | WT_DSXTAxx01=WT_DSXTA0201
|  | Phase:X_PUR_CHT02 CS_SEL_1: TA04_TO_CHT02 | N/A | WT_DSXTAxx01=WT_DSXTA0401
|  | Phase: X_PUR_CHT03 CS_SEL_1: TA05_TO_CHT03 | PD_OUT3 | WT_DSXTAxx01=WT_DSXTA0501

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| R_PT_SP1 | Yes | Tank pressure set point | real | barg | 0.2 | 0 | 2
| R_PT_SP1_DEV | NO | Deviation | real | barg | 0.05 | 0 | 1
| R_WT_SP | Yes | Weight low level | real | kg | 3 | 0 | 100
| R_DELAY_TM | NO | Time delay for tank empty. | int | sec | 5 | 0 | 100
| R_FIT_SP | YES | Flow of air through pipe | real | NL/min | 5 | 0 | 100
| R_DIRTY_VAL_SP | YES | Dirty Elapsed Timer | int | hr | 48 | 0 | 200
| R_DIRTY_WARN_SP | YES | Dirty Warn Timer | int | hr | 40 | 0 | 200
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description | Type | Eng.Unit | Step | Begin | End
| L_WT_PV_DEV(Note 4) |  | Weight reduction of loading tank |  | kg
| L_PT_PV |  | Tank pressure process value |  | barg
12 | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXPUR01/E-DSXPUR02/E-DSXPUR03/E-DSXPUR04/E-DSXPUR05/E-DSXPUR06 Emergency Stop
| Hold03 |  | PIT-DSXTA0201/PIT-DSXTA0401/PIT-DSXTA0501 fault
| Hold04 |  | WIT-DSXTA0201/WIT-DSXTA0401/WIT-DSXTA0501 fault
Note 4：L_WT_PV_DEV is equal to WT_DSXTAxx01 of S1030 minus WT_DSXTAxx01 of S1050.