## Cover Sheet
Phase Specification PH_P_GEL_INST
Shanghai Morimatsu Pharmaceutical Equipment Engineering Co.,Ltd No.29, Jinwen Road, Airport Industrial Park, Zhuqiao Town, Pudong, Shanghai |  |  | Innovent Biologics(Suzhou), Ltd 168 Dongping Streer, Suzhou Industrial Park, Suzhou, Jiangsu
Project |  |  | Document No. |  | Revision
M2 Project |  |  | PP20-0098-T-009682 |  | 2.0
| Initials | Date |  | Signature
Morimatsu prepared: | 吴婷 | 2021-04-26 |  | 吴婷
Morimatsu approved: | 张蓉蓉 | 2021-04-26 |  | 张蓉蓉
Innovent reviewed:
Innovent approved:

## Info Sheet
1. | Purpose
The Phase Specification provides the description of the process requirements for a Phase to be implemented in the DeltaV DCS Software. A separate Phase Specification will be provided for each individual Phase Class. The Phase Specification will be used as an input document for the implementation of the DCS application software and as a reference document for the execution of FAT and SAT.
2. | Method
The Phase Specification is subdivided in the following sections: - Description - SFC - Action Table - Input Parameter Table - Report Parameter table - HOLD table
The section "Description" provides a brief description of the purpose of the Phase. A table shows the assignment of the Phase to the Unit Class / Units at which the Phase can be exeuted, as well as the Equipment Module Classes that will be acquired by the Phase.
The section "SFC" shows the stepwise execution of the Phase in a Sequential Function Chart (SFC). The SFC shows all steps and transitions in a generic way. If required, and not covered in the Action Table, also special control actions will be shown in the SFC. The SFC is shown for the the S88 modes "Run", "Hold", and "Abort".
The section "Action Table" shows all control actions that will be executed from the Phase via Equipment Modules and Control Modules. The table specifies for each individual step of the Phase the EM Commands for the acquired Equipment Modules, as well as alarm settings and PID control loop settings.
The section "Input Parameter Table" shows all Input Parameters (IP) that are needed for the execution of the Phase. Indication is given if the Input Pameters (IP) can be deferred (yes/no) - Input Parameters that can be deferred can be used from operations/recipes and can be changed by the operators - Input Parameters that cannot be deferred are equipmemt parameters that cannot be changed from operations/recipes but are used as equipment parameters for commissioning
The section "Report Parameter Table" shows all Report Parameters (RP) that will be generated during phase execution and are mainly used for recording of single process values or process events at a specific time during phase execution. The table indicates if the Report Parameter shall be generated at the beginning or at the termination of the step.
The section "Hold Table" shows all process events that can force the Phase to Hold during phase execution.
3. | References
The settings for valves at the individual states of the Equipment Modules can be found in the document Equipment Module (EM) Specification.
4. | Naming Conventions
| Entity | Naming Convention |  |  | Example
| Phase | max. 16 characters, capital letters, _ for delimiter, EM_..... |  |  | PREPARE_MEDIA
| Step | max. 16 characters, _ for delimiter |  |  | HEAT_1
5. | Change Log
The Phase Specification is a living document, that will be updated as required. Changes to last version will be identified with text in red letters. Major revisions will be done for milestones in project execution. All intermediate versions are indicated by the major revision and the date of printing.
| Rev. | Date | Name | Description
| 0 | 2020-12-04 | 吴婷 | Draft for review
| 1.0 | 2021-03-03 | 吴婷 | 根据程序仿真修改
| 2.0 | 2021-04-26 | 吴婷 | 增加急停编号，删除效期参数。

## Description
6. | Description
The Phase is used for Install column of gel tank.
7. | Assignment
7.1 | Unit Classes
The Phase is assigned to the following Unit Class and Units (Instances)
| Unit Class | Units
| Slurry Tank匀浆罐 | 1500L Slurry TANK UNIT TA07
7.2 | Equipment Modules
The Phase will acquire the following Equipment Modules, which can be from the unit itself or from other units (Shared Equipment Modules)
EM's at Own Units
| Unit | Equiment Module
| Slurry Tank匀浆罐 | EM_GEL
AG01

## SFC_CHECK
8. | SFC Check Steps for RUN Logic

## SFC_RUN
8. | RUN Logic without Check Steps

## SFC_HOLD_ABORT
8. | HOLD and ABORT Logic

## Action Table
9. | Action Table
The following actions will be performed during the stepwise phase execution
|  | Phase | EM
|  | PH_P_GEL_INST | EM_DSXTA07 | AG-DSXTA0701
Step |  | Description | EM_GEL | AG01 | Report Record | Alarm Settings | Controller Settings | Other Actions
S9000 | EM_CHECK | EM检查，检查是否被占用，是否是空闲 Check if all the EM are free or not | N/A | N/A
S9010 | ERROR_ MESSAGE_1 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A
S9020 | STATE_CHECK | 状态检查，检查STATE是否正确 Check if the STATE is correct or not | N/A | N/A
S9030 | ERROR_ MESSAGE_2 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A
S9040 | ROUTE_CHECK | 路径检查，检查路径是否可用 Check if the ROUTE is available or not | N/A | N/A
S9050 | ERROR_ MESSAGE_3 | 提示是否继续或放弃 Prompt to continue or complete the phase | N/A | N/A
S9060 | ENABLE_HM&SM | 启用PHASE相关的报警 Enable Hold Monitor and Sentinel Monitor | N/A | N/A
S1010 | MSG | 检查管道，设备是否安装完成 Check if the pipe and equipment are ready? | N/A | N/A
S1020 | TARE_BALANCE | 称重清零 Tare balance | N/A | N/A
S1030 | VC_TK | 罐子抽真空 Tank vacuuming | VC_TK | STOP
S1040 | PD_IN | 打开进料阀进产品 Open inlet valves to feed product | PD_IN_TK | STOP
S1050 | BUF_IN1 | 进缓冲液 Feed buffer | BUF_IN_BOM | STOP
S1060 | PA_BLOW | 气吹 PA blow | PA_BLOW | STOP
S1070 | START_AG | 启动搅拌 Start agitator | PA_BLOW | START |  |  | Adjust the stirring speed according to the weight of the tank | Monitor torque in the whole process, motor overload and stop stirring automatically. Mixing starts at the lowest speed, then slowly accelerates to the working speed.
S1080 | BUF_CHANGE | 换液 Change buffer | BUF_CHANGE | ok |  |  | EM_GEL: WT_SP1=R_WT_SP1 WT_SP2=R_WT_SP2 WT_SP3=R_WT_SP3 WT_SP4=R_WT_SP4 WT_SP5=R_WT_SP5 | After buffer change is over ,vent until PT-DSXTA0701≤R_PT_SP3
S1090 | BUF_IN2 | 进缓冲液 Feed buffer | BUF_IN_BOM | STOP
S1100 | RECEIVE_BUF | 接收缓冲液 Receive buffer | BUF_IN_BOM | STOP
S1110 | MSG | 请确认是否循环 Please confirm whether to cycle or not? | CLOSE | STOP
S1120 | PA_BLOW | 气吹 PA blow | PA_BLOW | STOP
S1130 | START_AG | 启动搅拌 Start agitator | PA_BLOW | START |  |  | Adjust the stirring speed according to the weight of the tank | Monitor torque in the whole process, motor overload and stop stirring automatically. Mixing starts at the lowest speed, then slowly accelerates to the working speed.
S1140 | SAMPLING | 取样,测量匀浆比 Sampling， | CLOSE | START |  |  |  | Monitor torque in the whole process, motor overload and stop stirring automatically
S1150 | MSG | 请确认匀浆比是否合适 Please confirm whether The homogenization ratio is suitable or not? | CLOSE | START |  |  |  | Monitor torque in the whole process, motor overload and stop stirring automatically
S1160 | BUF_IN | 从罐顶进缓冲液 Feed buffer from J Tube. | BUF_IN | START |  |  |  | Monitor torque in the whole process, motor overload and stop stirring automatically
S1170 | MSG | 请确认是否立即装柱 Please confirm whether To install the column immediately or not? | CLOSE | START |  |  |  | Monitor torque in the whole process, motor overload and stop stirring automatically
S1180 | HOLD | 暂停 Hold | HOLD | HOLD
S1190 | PA_BLOW | 气吹 PA blow | PA_BLOW | STOP
S1200 | START_AG | 启动搅拌 Start agitator | PA_BLOW | START |  |  | Adjust the stirring speed according to the weight of the tank | Monitor torque in the whole process, motor overload and stop stirring automatically. Mixing starts at the lowest speed, then slowly accelerates to the working speed.
S1210 | MSG | 检查管道，设备是否安装完成 Check if the pipe and equipment are ready? | CLOSE | START |  |  |  | Monitor torque in the whole process, motor overload and stop stirring automatically
S1220 | PD_OUT | 出料 Product out | PD_OUT | START |  |  |  | Monitor torque in the whole process, motor overload and stop stirring automatically
S1230 | CLOSE | 关闭所有阀门。 Close all valve. | CLOSE | STOP
S1240 | SET_STATE | 重置状态 set state | CLOSE | STOP |  |  |  | Source Tank = Dirty
S7010 | HOLD | 暂停 pause | HOLD | HOLD
S8010 | ABORT | 关闭所有阀门。 Close all valve. | CLOSE | CLOSE
S8020 | SET_STATE | 重置状态 set state | CLOSE | CLOSE |  |  |  | Source Tank = Process

## ParameterHold Tables
10. | Input Parameter (IP) Table
The following Input Parameters (IP)will be used during the execution of the Phase. All numerical values are floating point format.
| Parameter | Deferred | Description | Type | Eng. Unit | Default | min | max
| R_VC_SP | YES | Vacuum set point | real | barg | PENDING | -1.5 | 0
| R_VC_SP_DEV | NO | Vacuum deviation | real | barg | 0 | -1 | 1
| R_PT_SP3 | Yes | Tank pressure set point when vent | real | barg | 0 | 0 | 2
| R_WT_SP1 | YES | WT-DSXTA0701 set point | real | kg | 775 | 0 | 1500
| R_WT_SP2 | YES | WT-DSXTA0701 set point | real | kg | 302 | 0 | 1500
| R_WT_SP3 | YES | WT-DSXTA0701 set point | real | kg | 25 | 0 | 1500
| R_WT_SP4 | YES | WT-DSXTA0701 set point | real | kg | 25 | 0 | 1500
| R_WT_SP5 | YES | WT-DSXTA0701 set point | real | kg | 25 | 0 | 1500
| R_WT_SP6 | YES | WT-DSXTA0701 set point | real | kg | PENDING | 0 | 1500
| R_WT_SP7 | YES | WT-DSXTA0701 set point | real | kg | PENDING | 0 | 1500
| R_WT_SP8 | YES | WT-DSXTA0701 set point | real | kg | PENDING | 0 | 1500
| R_L_WT_SP | YES | WT-DSXTA0701 minimum set point | real | kg | PENDING | 0 | 1500
| R_TM_AG1 | NO | Time for mixing | real | min | PENDING | 0 | 200
| R_TM_AG2 | NO | Time for mixing | real | min | PENDING | 0 | 200
| R_TM_AG3 | NO | Time for mixing | real | min | PENDING | 0 | 200
| R_SPD_AG | YES | Speed of agitator | real | rpm | PENDING | 0 | 120
| R_DIRTY_VAL_SP | YES | Dirty Elapsed Timer | int | hr | 48 | 0 | 200
| R_DIRTY_WARN_SP | YES | Dirty Warn Timer | int | hr | 40 | 0 | 200
11. | Report Parameter (RP) Table
The following Report Parameters (RP) are generated during the execution of the Phase from the defined steps, either at the begiining of the step or at the termination of the step. All numerical values are floating point format.
| Parameter |  | Description |  | Eng.Unit | Step | Begin | End
| L_WT_INPUT1 |  | BUF_IN input value 1 |  | kg
| L_WT_INPUT2 |  | BUF_IN input value 2 |  | kg
12. | HOLD Table
The follwing events or process conditionds will force the Phase to HOLD.
| Code |  | Description
| Hold01 |  | Operator command
| Hold02 |  | E-DSXPUR01/E-DSXPUR02/E-DSXPUR03/E-DSXPUR04/E-DSXPUR05/E-DSXPUR06 Emergency Stop
| Hold03 |  | WIT fault
| Hold04 |  | AG fault